## Summary
Technical and Environmental Due Diligence of Hanjin Shipyard
for Cerberus Capital Management
CAPEX Optimization of Facilities - Phase 2
As of 31 March 2020
USER | 0 |  | (+/-) | 1-2 |  | (+/-) | 3-5 |  | (+/-) | 6-10 |  | (+/-) | 11-25 |  | (+/-)
| Phase 1 | Phase 2 |  | Phase 1 | Phase 2 |  | Phase 1 | Phase 2 |  | Phase 1 | Phase 2 |  | Phase 1 | Phase 2
Navy | 5295535 | 6294240 | 998705 | 439665 | 401120 | -38545 | 3040600 | 840140 | -2200460 | 973490 | 868330 | -105160 | 883870 | 5683620 | 4799750
Austal | 10715030 | 8436320 | -2278710 | 1581000 | 49570 | -1531430 | 1077500 | 896360 | -181140 | 0 | 1399020 | 1399020 | 1017130 | 3979950 | 2962820
Dock 6 | 6264090 | 7818070 | 1553980 | 3264407.65 | 39480 | -3224927.65 | 0 | 870040 | 870040 | 0 | 75660 | 75660 | 5483110 | 3288150 | -2194960
Tenant 3 | 2480240 | 2864180 | 383940 | 2177200 | 0 | -2177200 | 30000 | 30000 | 0 | 0 | 152010 | 152010 | 242760 | 512400 | 269640
Shared | 154340 | 7472850 | 7318510 | 8900 | 43620 | 34720 | 117000 | 0 | -117000 | 0 | 5400 | 5400 | 1610 | 7010 | 5400
Total | 24909235 | 32885660 | 7976425 | 7471172.65 | 533790 | -6937382.65 | 4265100 | 2636540 | -1628560 | 973490 | 2500420 | 1526930 | 7628480 | 13471130 | 5842650
Total Cost Distribution per work type
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 138830 | 0 | 0 | 0 | 0 | 138830
Demolition | 0 | 0 | 0 | 917970 | 0 | 917970
Electrical System | 1711160 | 0 | 0 | 0 | 3376710 | 5087870
Environmental | 180000 | 0 | 30000 | 0 | 0 | 210000
Fire Protection System | 858290 | 0 | 0 | 0 | 0 | 858290
HVAC | 781570 | 156870 | 2453440 | 567360 | 5048010 | 9007250
Interior | 1202470 | 156520 | 94090 | 377330 | 1055710 | 2886120
Mechanical System | 0 | 7850 | 0 | 0 | 0 | 7850
Perimeter Fence | 5352950 | 0 | 0 | 0 | 0 | 5352950
Plumbing System | 550610 | 0 | 30330 | 0 | 0 | 580940
Roof | 1057030 | 0 | 0 | 410070 | 3902460 | 5369560
Structural Elements | 413020 | 0 | 0 | 0 | 0 | 413020
Structural Upgrade | 9597420 | 0 | 0 | 0 | 0 | 9597420
Vertical Transportation | 8830 | 0 | 0 | 0 | 88240 | 97070
Miscellaneous | 3384050 | 184070 | 28680 | 0 | 0 | 3596800
Contingencies | 2809390 | 10530 | 0 | 84500 | 0 | 2904420
Preliminaries | 3109910 | 11580 | 0 | 92960 | 0 | 3214450
Engineering and Management | 1730130 | 6370 | 0 | 50230 | 0 | 1786730
Total | 32885660 | 533790 | 2636540 | 2500420 | 13471130 | 52027540
Navy
Cost Distribution per work type (Navy)
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 138830 | 0 | 0 | 0 | 0 | 138830
Demolition | 0 | 0 | 0 | 89420 | 0 | 89420
Electrical System | 714550 | 0 | 0 | 0 | 2895040 | 3609590
Environmental | 32500 | 0 | 0 | 0 | 0 | 32500
Fire Protection System | 11770 | 0 | 0 | 0 | 0 | 11770
HVAC | 382320 | 156870 | 781130 | 450910 | 1511180 | 3282410
Interior | 919590 | 106950 | 0 | 188750 | 753160 | 1968450
Mechanical System | 0 | 7850 | 0 | 0 | 0 | 7850
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 147570 | 0 | 30330 | 0 | 0 | 177900
Roof | 449230 | 0 | 0 | 135700 | 436000 | 1020930
Structural Elements | 367180 | 0 | 0 | 0 | 0 | 367180
Structural Upgrade | 800420 | 0 | 0 | 0 | 0 | 800420
Vertical Transportation | 8830 | 0 | 0 | 0 | 88240 | 97070
Miscellaneous | 736090 | 110270 | 28680 | 0 | 0 | 875040
Contingencies | 586130 | 7090 | 0 | 1640 | 0 | 594860
Preliminaries | 644750 | 7800 | 0 | 1810 | 0 | 654360
Engineering and Management | 354480 | 4290 | 0 | 100 | 0 | 358870
Total | 6294240 | 401120 | 840140 | 868330 | 5683620 | 14087450
Austal
Cost Distribution per work type (Austal)
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 828550 | 0 | 828550
Electrical System | 494340 | 0 | 0 | 0 | 215810 | 710150
Environmental | 32500 | 0 | 0 | 0 | 0 | 32500
Fire Protection System | 434040 | 0 | 0 | 0 | 0 | 434040
HVAC | 247620 | 0 | 871340 | 110950 | 1929390 | 3159300
Interior | 130440 | 49570 | 25020 | 113020 | 157920 | 475970
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 52970 | 0 | 0 | 0 | 0 | 52970
Roof | 207020 | 0 | 0 | 122360 | 1663640 | 1993020
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 3906300 | 0 | 0 | 0 | 0 | 3906300
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 911080 | 0 | 0 | 0 | 0 | 911080
Contingencies | 730430 | 0 | 0 | 82860 | 0 | 813290
Preliminaries | 803460 | 0 | 0 | 91150 | 0 | 894610
Engineering and Management | 459890 | 0 | 0 | 50130 | 0 | 510020
Total | 8410090 | 49570 | 896360 | 1399020 | 3966760 | 14721800
0.26534
0.34998
Dock 6
Cost Distribution per work type (Dock6)
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 453150 | 0 | 0 | 0 | 53270 | 506420
Environmental | 32500 | 0 | 0 | 0 | 0 | 32500
Fire Protection System | 210330 | 0 | 0 | 0 | 0 | 210330
HVAC | 151630 | 0 | 800970 | 5500 | 1607440 | 2565540
Interior | 147040 | 0 | 69070 | 70160 | 139230 | 425500
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 6870 | 0 | 0 | 0 | 0 | 6870
Roof | 84620 | 0 | 0 | 0 | 1501400 | 1586020
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 3906950 | 0 | 0 | 0 | 0 | 3906950
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 970590 | 39480 | 0 | 0 | 0 | 1010070
Contingencies | 694600 | 0 | 0 | 0 | 0 | 694600
Preliminaries | 764050 | 0 | 0 | 0 | 0 | 764050
Engineering and Management | 421970 | 0 | 0 | 0 | 0 | 421970
Total | 7844300 | 39480 | 870040 | 75660 | 3301340 | 12130820
Tenant 3
Cost Distribution per work type (Tenant 3)
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 19620 | 0 | 0 | 0 | 210980 | 230600
Environmental | 82500 | 0 | 30000 | 0 | 0 | 112500
Fire Protection System | 202150 | 0 | 0 | 0 | 0 | 202150
HVAC | 0 | 0 | 0 | 0 | 0 | 0
Interior | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 44120 | 0 | 0 | 0 | 0 | 44120
Roof | 262230 | 0 | 0 | 152010 | 301420 | 715660
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 940610 | 0 | 0 | 0 | 0 | 940610
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 696550 | 0 | 0 | 0 | 0 | 696550
Contingencies | 227850 | 0 | 0 | 0 | 0 | 227850
Preliminaries | 250630 | 0 | 0 | 0 | 0 | 250630
Engineering and Management | 137920 | 0 | 0 | 0 | 0 | 137920
Total | 2864180 | 0 | 30000 | 152010 | 512400 | 3558590
Shared
Cost Distribution per work type (Shared)
Work Type | Years |  |  |  |  | Total
| 0 | 1-2 | 3-5 | 6-10 | 11-25
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 29500 | 0 | 0 | 0 | 1610 | 31110
Environmental | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 0 | 0 | 0 | 0 | 0 | 0
Interior | 5400 | 0 | 0 | 5400 | 5400 | 16200
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 5352950 | 0 | 0 | 0 | 0 | 5352950
Plumbing System | 299080 | 0 | 0 | 0 | 0 | 299080
Roof | 53930 | 0 | 0 | 0 | 0 | 53930
Structural Elements | 45840 | 0 | 0 | 0 | 0 | 45840
Structural Upgrade | 43140 | 0 | 0 | 0 | 0 | 43140
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 69740 | 34320 | 0 | 0 | 0 | 104060
Contingencies | 570380 | 3440 | 0 | 0 | 0 | 573820
Preliminaries | 647020 | 3780 | 0 | 0 | 0 | 650800
Engineering and Management | 355870 | 2080 | 0 | 0 | 0 | 357950
Total | 7472850 | 43620 | 0 | 5400 | 7010 | 7528880

## Analysis
Technical and Environmental Due Diligence of Hanjin Shipyard
for Cererus Capital Management
CAPEX Optimization of Facilities - Phase 2
As of 30 March 2020
Facilities | User | Area | 0 |  | 1-2 |  | 3-5 |  | 6-10 |  | 11-25 |  | Total
|  |  | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2
Air Compressed Room - 1 | Dock 6 | 1342 | 33320 | 50810 | 0 | 39480 | 0 | 0 | 0 | 0 | 0 | 0 | 33320 | 90290 | 56970
Air Compressed Room - 2,3 | Austal | 382 | 95200 | 19050 | 0 | 0 | 0 | 0 | 0 | 0 | 50190 | 50190 | 145390 | 69240 | -76150
Assembly shelter (6 nos) | Austal | 11130 | 773610 | 427030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318140 | 773610 | 745170 | -28440
Assembly shop (A) | Austal | 27390 | 537350 | 888260 | 0 | 0 | 0 | 0 | 0 | 0 | 151060 | 322240 | 688410 | 1210500 | 522090
Assembly shop (B) | Austal | 40562 | 1170090 | 1333770 | 143700 | 0 | 0 | 0 | 0 | 0 | 318770 | 318140 | 1632560 | 1651910 | 19350
Assembly Shop (C) | Dock 6 | 27025 | 779570 | 628680 | 635900 | 0 | 0 | 0 | 0 | 0 | 166330 | 529910 | 1581800 | 1158590 | -423210
Assembly Shop (D) | Navy | 11880 | 342700 | 166820 | 0 | 0 | 0 | 0 | 57120 | 129420 | 16030 | 70000 | 415850 | 366240 | -49610
Barracks - Accommodation | Navy | 166 | 0 | 4740 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 2000 | 0 | 8740 | 8740
Barracks - Admin | Navy | 1500 | 0 | 128120 | 0 | 0 | 0 | 0 | 0 | 53640 | 0 | 58060 | 0 | 239820 | 239820
Barracks - B | Navy | 780 | 0 | 97960 | 0 | 0 | 0 | 0 | 489000 | 73980 | 6790 | 76280 | 495790 | 248220 | -247570
Barracks - C | Navy | 1300 | 0 | 207840 | 0 | 0 | 0 | 0 | 0 | 114280 | 0 | 118110 | 0 | 440230 | 440230
Barracks - D | Navy | 1050 | 0 | 156410 | 0 | 0 | 0 | 0 | 0 | 90300 | 0 | 93390 | 0 | 340100 | 340100
Barracks - E | Navy | 1300 | 0 | 150950 | 0 | 0 | 0 | 0 | 0 | 81630 | 0 | 85460 | 0 | 318040 | 318040
Barracks - F | Navy | 700 | 0 | 43620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43620 | 43620
Barracks - G1 | Navy | 1100 | 0 | 108830 | 0 | 0 | 0 | 0 | 0 | 53050 | 0 | 312420 | 0 | 474300 | 474300
Barracks - G2 | Navy | 1500 | 0 | 120050 | 0 | 0 | 0 | 0 | 0 | 53640 | 0 | 58060 | 0 | 231750 | 231750
Barracks - J | Navy | 210 | 0 | 13100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13100 | 13100
Barracks - K | Navy | 2600 | 0 | 64790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64790 | 64790
Barracks - Romanian | Navy | 210 | 0 | 13100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13100 | 13100
Blasting & Painting Shop B | Austal | 13895 | 1001900 | 398930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20230 | 1001900 | 419160 | -582740
Blasting & Painting Shop C | Dock 6 | 15001 | 1031330 | 411100 | 0 | 0 | 0 | 0 | 0 | 0 | 741390 | 20230 | 1772720 | 431330 | -1341390
Blasting & Painting Shop D | Dock 6 | 15008 | 1031500 | 411290 | 353117.65 | 0 | 0 | 0 | 0 | 0 | 741390 | 20230 | 2126007.65 | 431520 | -1694487.65
Blasting & Painting Shop E | Navy | 5913 | 170570 | 66690 | 0 | 0 | 0 | 0 | 284280 | 0 | 0 | 0 | 454850 | 66690 | -388160
Blasting Shop A | Dock 6 | 5485 | 158230 | 151220 | 0 | 0 | 0 | 0 | 0 | 5500 | 7420 | 12920 | 165650 | 169640 | 3990
CO2 Plant | Navy | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92970 | 0 | 0 | 0 | 92970 | 92970
Cable Cutting | Navy | 1250 | 0 | 155300 | 0 | 0 | 0 | 0 | 0 | 0 | 2730 | 150000 | 2730 | 305300 | 302570
Canteen-Romanian | Navy | 220 | 0 | 0 | 0 | 27420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27420 | 27420
Catering Center | Navy | 6186 | 249500 | 420740 | 74900 | 246370 | 1077000 | 344070 | 130390 | 0 | 16450 | 593280 | 1548240 | 1604460 | 56220
Convenience Store building | Navy | 502 | 0 | 0 | 63100 | 62550 | 0 | 0 | 0 | 0 | 0 | 0 | 63100 | 62550 | -550
Dhouse Shelter | Tenant 3 | 15180 | 472190 | 613050 | 638200 | 0 | 0 | 0 | 0 | 84710 | 36540 | 70000 | 1146930 | 767760 | -379170
Electric Steel Outfitting Shop | Navy | 3300 | 341030 | 394630 | 0 | 0 | 0 | 0 | 0 | 0 | 2730 | 85690 | 343760 | 480320 | 136560
Electric Steel Outfitting Shop (Building at the back) | Navy | 1000 | 230500 | 178650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1480 | 230500 | 180130 | -50370
Field Office 1 | Austal | 1346 | 11700 | 239400 | 42000 | 0 | 0 | 199840 | 0 | 19420 | 0 | 403260 | 53700 | 861920 | 808220
Field Office 10 | Dock 6 | 1079 | 8900 | 198070 | 32100 | 0 | 0 | 158820 | 0 | 20360 | 0 | 325300 | 41000 | 702550 | 661550
Field Office 11A | Dock 6 | 845 | 10000 | 214580 | 36100 | 0 | 0 | 126310 | 0 | 4280 | 0 | 246950 | 46100 | 592120 | 546020
Field Office 11B | Dock 6 | 1300 | 11800 | 327880 | 42400 | 0 | 0 | 191190 | 0 | 7360 | 0 | 374440 | 54200 | 900870 | 846670
Field Office 12 | Dock 6 | 785 | 12500 | 149200 | 45200 | 0 | 0 | 117480 | 0 | 14020 | 0 | 239740 | 57700 | 520440 | 462740
Field Office 13 | Navy | 300 | 5200 | 72090 | 18500 | 12360 | 0 | 0 | 0 | 16390 | 0 | 41110 | 23700 | 141950 | 118250
Field Office 14 | Navy | 310 | 5200 | 27560 | 18500 | 0 | 0 | 0 | 0 | 46610 | 0 | 50260 | 23700 | 124430 | 100730
Field Office 15 | Austal | 400 | 5200 | 71860 | 18500 | 0 | 0 | 54120 | 0 | 12360 | 0 | 71190 | 23700 | 209530 | 185830
Field Office 2 | Austal | 640 | 7500 | 208090 | 27000 | 8480 | 0 | 97420 | 0 | 5900 | 0 | 209220 | 34500 | 529110 | 494610
Field Office 2A | Austal | 720 | 8500 | 210030 | 30500 | 8480 | 0 | 97420 | 0 | 5900 | 0 | 209220 | 39000 | 531050 | 492050
Field Office 3 | Austal | 432 | 5200 | 111720 | 18500 | 5090 | 0 | 59530 | 0 | 3680 | 0 | 127830 | 23700 | 307850 | 284150
Field Office 5 | Navy | 432 | 5200 | 71210 | 18500 | 5090 | 0 | 59530 | 0 | 3840 | 0 | 127990 | 23700 | 267660 | 243960
Field Office 5A | Dock 6 | 594 | 7100 | 100290 | 25400 | 0 | 0 | 88170 | 0 | 4720 | 0 | 174070 | 32500 | 367250 | 334750
Field Office 6 | Austal | 780 | 6100 | 144050 | 9600 | 0 | 0 | 114710 | 0 | 15360 | 0 | 235600 | 15700 | 509720 | 494020
Field Office 6a | Austal | 630 | 22000 | 163240 | 34700 | 9530 | 0 | 0 | 0 | 129050 | 0 | 126660 | 56700 | 428480 | 371780
Field Office 7 | Austal | 575 | 6800 | 100590 | 24500 | 6770 | 0 | 78480 | 0 | 13180 | 0 | 168450 | 31300 | 367470 | 336170
Field Office 8 | Austal | 953 | 7500 | 233080 | 27000 | 11220 | 0 | 194840 | 0 | 19120 | 0 | 535880 | 34500 | 994140 | 959640
Field Office 9 | Dock 6 | 1265 | 12100 | 232170 | 43500 | 0 | 0 | 188070 | 0 | 19420 | 0 | 380670 | 55600 | 820330 | 764730
Filtration Plant | Shared | 350 | 0 | 0 | 8900 | 43620 | 0 | 0 | 0 | 0 | 0 | 0 | 8900 | 43620 | 34720
Fire Station | Dock 6 | 225 | 0 | 31230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31230 | 31230
Gasoline Station | Navy | 300 | 0 | 37400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37400 | 37400
Guest House | Navy | 2610 | 855570 | 645320 | 0 | 0 | 0 | 156870 | 0 | 6180 | 572020 | 207490 | 1427590 | 1015860 | -411730
Hatch cover Shelter | Tenant 3 | 16000 | 935300 | 784280 | 744500 | 0 | 0 | 0 | 0 | 67300 | 49840 | 70000 | 1729640 | 921580 | -808060
Helicopter Hangar | Navy | 900 | 0 | 56080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56080 | 56080
Hull Shop (A) | Austal | 37736 | 1291740 | 1199130 | 780400 | 0 | 0 | 0 | 0 | 0 | 320570 | 443960 | 2392710 | 1643090 | -749620
Hull Shop B | Dock 6 | 38920 | 342960 | 1169510 | 744500 | 0 | 0 | 0 | 0 | 0 | 283930 | 152630 | 1371390 | 1322140 | -49250
Main Gate | Navy | 1342 | 39470 | 50810 | 0 | 39480 | 0 | 0 | 0 | 0 | 0 | 0 | 39470 | 90290 | 50820
Main Generator Room | Navy | 1000 | 0 | 1900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1985300 | 0 | 1987200 | 1987200
Main Office | Navy | 15000 | 455900 | 1398200 | 0 | 0 | 1963600 | 279670 | 0 | 44120 | 12600 | 855760 | 2432100 | 2577750 | 145650
Maintenance Shop | Dock 6 | 1500 | 43120 | 41130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43120 | 41130 | -1990
Nagyantok Material Store and Bond shop | Tenant 3 | 9500 | 0 | 6250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250 | 6250
Nagyantok Outfitting Shop A | Tenant 3 | 3950 | 0 | 246020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246020 | 246020
Nagyantok Procurement Storage shop | Tenant 3 | 2100 | 0 | 26170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26170 | 26170
Nagyantok Segragation Area | Tenant 3 | 2500 | 0 | 31160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31160 | 31160
Nagyantok Stock office | Tenant 3 | 60 | 0 | 7490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7490 | 7490
Nagyantok Stock Room 1 | Tenant 3 | 360 | 0 | 44860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44860 | 44860
Nagyantok Stock Room 2 | Tenant 3 | 300 | 0 | 37400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37400 | 37400
Nagyantok Warehouse | Tenant 3 | 650 | 0 | 28370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28370 | 28370
No.5 Dock Shelter | Austal | 4950 | 172700 | 184980 | 0 | 0 | 0 | 0 | 0 | 0 | 49840 | 82550 | 222540 | 267530 | 44990
Outfitting Shop | Austal | 5600 | 0 | 217660 | 0 | 0 | 0 | 0 | 0 | 109810 | 0 | 0 | 0 | 327470 | 327470
Paint Can Stock Area | Dock 6 | 1550 | 112570 | 42500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112570 | 42500 | -70070
Painting Shop A -1 | Navy | 860 | 0 | 29820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42160 | 0 | 71980 | 71980
Painting Shop A Ext. | Dock 6 | 10500 | 386990 | 287760 | 253100 | 0 | 0 | 0 | 0 | 0 | 659450 | 0 | 1299540 | 287760 | -1011780
Panel Shop | Dock 6 | 54983 | 1586040 | 1536870 | 0 | 0 | 0 | 0 | 0 | 0 | 2717460 | 539050 | 4303500 | 2075920 | -2227580
Pipe Manufacture Shop A&B | Navy | 10462 | 905370 | 181270 | 246165 | 0 | 0 | 0 | 0 | 0 | 14140 | 478830 | 1165675 | 660100 | -505575
Piping Pre-treatment building Galva | Navy | 2900 | 1137325 | 1021720 | 0 | 0 | 0 | 0 | 0 | 0 | 145600 | 0 | 1282925 | 1021720 | -261205
Piping Shelter | Navy | 1000 | 0 | 14100 | 0 | 7850 | 0 | 0 | 0 | 0 | 0 | 49020 | 0 | 70970 | 70970
Powerplant and Control Station | Shared | 1100 | 154340 | 207280 | 0 | 0 | 117000 | 0 | 0 | 5400 | 1610 | 7010 | 272950 | 219690 | -53260
Pre Treatment Shop A | Austal | 4662 | 92015 | 127790 | 68600 | 0 | 0 | 0 | 0 | 0 | 4305 | 18290 | 164920 | 146080 | -18840
Pre Treatment Shop B | Austal | 3362 | 92015 | 92160 | 68600 | 0 | 0 | 0 | 0 | 0 | 4305 | 13190 | 164920 | 105350 | -59570
Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | Dock 6 | 18983 | 168920 | 605440 | 649200 | 0 | 0 | 0 | 0 | 0 | 61690 | 74450 | 879810 | 679890 | -199920
Pre-erection area (6 nos) - No. 5 Dock Shelter | Austal | 17220 | 349320 | 582970 | 0 | 0 | 0 | 0 | 0 | 12550 | 13790 | 70000 | 363110 | 665520 | 302410
Pre-Outfitting Shop (A) | Austal | 8805 | 254000 | 266880 | 143700 | 0 | 0 | 0 | 0 | 0 | 19600 | 69060 | 417300 | 335940 | -81360
Pre-Outfitting Shop (B) | Dock 6 | 5734 | 164770 | 174450 | 134400 | 0 | 0 | 0 | 0 | 0 | 32220 | 67460 | 331390 | 241910 | -89480
Production Center 1/Hospital Building/Substation 8 | Austal | 10564 | 4255220 | 0 | 0 | 0 | 1077500 | 0 | 0 | 1052690 | 0 | 0 | 5332720 | 1052690 | -4280030
Samandra - Container Shop | Tenant 3 | 1542 | 0 | 28670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28670 | 28670
Samandra - Maintenance Shop/Office | Tenant 3 | 1650 | 0 | 192080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192080 | 192080
Samandra - Shop B | Tenant 3 | 2300 | 0 | 6250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250 | 6250
Samandra - Warehouse | Tenant 3 | 2301 | 0 | 20580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20580 | 20580
Sewage Treatment Plant | Shared | 1120 | 0 | 296250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296250 | 296250
Shared Utilities - Electricity | Shared | 0 | 0 | 37500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37500 | 37500
Shared Utilities - Water | Shared | 0 | 0 | 130880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130880 | 130880
Shared Utilities - Fence | Shared | 0 | 0 | 6800940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6800940 | 6800940
Shelter 712 | Navy | 1100 | 0 | 41120 | 0 | 0 | 0 | 0 | 12700 | 6280 | 0 | 70000 | 12700 | 117400 | 104700
Shelter for Piping | Navy | 2090 | 519500 | 22940 | 0 | 0 | 0 | 0 | 0 | 0 | 94290 | 70000 | 613790 | 92940 | -520850
Slope protection | Tenant 3 | 0 | 50000 | 78010 | 0 | 0 | 30000 | 30000 | 0 | 0 | 0 | 0 | 80000 | 108010 | 28010
Spill Prevention Kits/Secondary Containment Tenant 3 | Tenant 3 | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32500 | 45450 | 12950
Spill Prevention Kits/Secondary Containment Austal | Austal | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32500 | 45450 | 12950
Spill Prevention Kits/Secondary Containment Dock 6 | Dock 6 | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32500 | 45450 | 12950
Spill Prevention Kits/Secondary Containment Navy | Navy | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32500 | 45450 | 12950
Steel Stock Yard | Dock 6 | 37275 | 0 | 92880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92880 | 92880
Sub Assembly Shop | Austal | 15560 | 378400 | 537410 | 143700 | 0 | 0 | 0 | 0 | 0 | 80780 | 122040 | 602880 | 659450 | 56570
Sub Station #10 | Dock 6 | 207 | 0 | 26370 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 26860 | 26370
Sub station #11 | Austal | 800 | 0 | 44870 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 45360 | 44870
Sub station #12 | Austal | 735 | 0 | 67410 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 67900 | 67410
Sub Station #13 | Austal | 371 | 0 | 40220 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 40710 | 40220
Sub Station #14 | Austal | 612 | 0 | 58220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 58710 | 58710
Sub Station #15 | Austal | 332 | 0 | 37290 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 37780 | 37290
Sub Station #16 | Austal | 360 | 0 | 30170 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 30660 | 30170
Sub station #17 | Austal | 460 | 0 | 46860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 47350 | 47350
Sub station #20 | Austal | 325 | 0 | 36780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 37270 | 37270
Sub station #21 | Dock 6 | 1300 | 0 | 44870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 45360 | 45360
Sub station #22 | Dock 6 | 760 | 0 | 69280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 69770 | 69770
Sub station #22-1 | Dock 6 | 685 | 0 | 29550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 30040 | 30040
Sub Station #23 | Dock 6 | 410 | 0 | 22700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 23190 | 23190
Sub Station #24 | Dock 6 | 340 | 0 | 20950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 21440 | 21440
Sub station #25 | Dock 6 | 325 | 0 | 36780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 37270 | 37270
Sub station #26 | Dock 6 | 760 | 0 | 69280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 69770 | 69770
Sub Station #3 | Austal | 390 | 0 | 30930 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 31420 | 30930
Sub Station #30 | Dock 6 | 890 | 0 | 34650 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 35140 | 34650
Sub Station #31 | Navy | 320 | 0 | 36400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 36890 | 36890
Sub Station #32 | Dock 6 | 800 | 0 | 72270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 72760 | 72760
Sub Station #33 | Navy | 685 | 0 | 29550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 30040 | 30040
Sub Station #34 | Dock 6 | 260 | 0 | 18960 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 19450 | 18960
Sub Station #35 | Navy | 260 | 0 | 18960 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 19450 | 18960
Sub Station #36 | Tenant 3 | 400 | 0 | 42370 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 42860 | 42370
Sub Station #37 | Austal | 250 | 0 | 20560 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 21050 | 20560
Sub Station #38 | Tenant 3 | 270 | 0 | 32660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 33150 | 33150
Sub Station #9 | Austal | 360 | 0 | 39380 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 490 | 39870 | 39380
Sub-Assembly Shop (94 bay) | Tenant 3 | 10800 | 311540 | 207970 | 254200 | 0 | 0 | 0 | 0 | 0 | 14560 | 281770 | 580300 | 489740 | -90560
T-BHD Shelter | Tenant 3 | 11430 | 678710 | 385090 | 540300 | 0 | 0 | 0 | 0 | 0 | 141330 | 89650 | 1360340 | 474740 | -885600
Tool Shop | Austal | 985 | 0 | 36830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36830 | 36830
Waste Matter/Scrap Iron Stock | Dock 6 | 986 | 0 | 97180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97180 | 97180
Welding Inspection Shop | Austal | 5000 | 138470 | 143270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39220 | 138470 | 182490 | 44020
Welding Shop (B) | Dock 6 | 10600 | 329870 | 372720 | 269490 | 0 | 0 | 0 | 0 | 0 | 70360 | 124710 | 669720 | 497430 | -172290
|  | Total | 24909235 | 32885660 | 7471172.65 | 533790 | 4265100 | 2636540 | 973490 | 2500420 | 7628480 | 13471130 | 45247477.65 | 52027540 | 6780062.35
|  | +/- | 7976425 |  | -6937382.65 |  | -1628560 |  | 1526930 |  | 5842650
User | Total no. of facilities | Total Area (m2)
Austal | 36 | 219274
Dock 6 | 33 | 257722
Shared | 6 | 2570
Navy | 40 | 85738
Tenant 3 | 20 | 81293
Facilities | 0 |  |  |  |  | 1-2 |  |  |  |  | 3-5 |  |  |  |  | 6-10 |  |  |  |  | 11-25
| Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 138830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138830 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89420 | 0 | 0 | 0 | 0
Electrical System | 714550 | 494340 | 453150 | 19620 | 29500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2895040 | 215810 | 53270 | 210980 | 1610 | 3609590 | 710150 | 506420 | 230600 | 31110
Environmental | 32500 | 32500 | 32500 | 82500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32500 | 32500 | 32500 | 82500 | 0
Fire Protection System | 11770 | 434040 | 210330 | 202150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11770 | 434040 | 210330 | 202150 | 0
HVAC | 382320 | 247620 | 151630 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 781130 | 871340 | 800970 | 0 | 0 | 450910 | 0 | 0 | 0 | 0 | 1511180 | 1929390 | 1607440 | 0 | 0 | 2501280 | 2177010 | 1759070 | 0 | 0
Interior | 919590 | 130440 | 147040 | 0 | 5400 | 106950 | 49570 | 0 | 0 | 0 | 0 | 25020 | 69070 | 0 | 0 | 188750 | 46760 | 0 | 0 | 0 | 753160 | 157920 | 139230 | 0 | 5400 | 1968450 | 384690 | 286270 | 0 | 10800
Mechanical System | 0 | 0 | 0 | 0 | 0 | 7850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7850 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 5352950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5352950
Plumbing System | 147570 | 52970 | 6870 | 44120 | 299080 | 0 | 0 | 0 | 0 | 0 | 30330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147570 | 52970 | 6870 | 44120 | 299080
Roof | 449230 | 207020 | 84620 | 262230 | 53930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135700 | 122360 | 0 | 152010 | 0 | 436000 | 1663640 | 1501400 | 301420 | 0 | 1020930 | 1993020 | 1586020 | 715660 | 53930
Structural Elements | 367180 | 0 | 0 | 0 | 45840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367180 | 0 | 0 | 0 | 45840
Structural Upgrade | 800420 | 3906300 | 3906950 | 940610 | 43140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800420 | 3906300 | 3906950 | 940610 | 43140
Vertical Transportation | 8830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88240 | 0 | 0 | 0 | 0 | 97070 | 0 | 0 | 0 | 0
Miscellaneous | 736090 | 911080 | 970590 | 696550 | 69740 | 110270 | 0 | 39480 | 0 | 34320 | 28680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846360 | 911080 | 1010070 | 696550 | 104060
Contingencies | 586130 | 730430 | 694600 | 227850 | 570380 | 7090 | 0 | 0 | 0 | 3440 | 0 | 0 | 0 | 0 | 0 | 1640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594860 | 730430 | 694600 | 227850 | 573820
Preliminaries | 644750 | 803460 | 764050 | 250630 | 647020 | 7800 | 0 | 0 | 0 | 3780 | 0 | 0 | 0 | 0 | 0 | 1810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654360 | 803460 | 764050 | 250630 | 650800
Engineering and Management | 354480 | 459890 | 421970 | 137920 | 355870 | 4290 | 0 | 0 | 0 | 2080 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358870 | 459890 | 421970 | 137920 | 357950
Total | 6294240 | 8410090 | 7844300 | 2864180 | 7472850 | 401120 | 49570 | 39480 | 0 | 43620 | 840140 | 896360 | 870040 | 30000 | 0 | 868330 | 169120 | 0 | 152010 | 0 | 5683620 | 3966760 | 3301340 | 512400 | 7010 | 13247310 | 12595540 | 11185120 | 3528590 | 7523480

## 0-25year
Facilities | Intervention Year | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 0 | 138830 | 0 | 0 | 0 | 0 | 138830
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 0 | 714550 | 494340 | 453150 | 19620 | 29500 | 1711160
Environmental | 0 | 32500 | 32500 | 32500 | 82500 | 0 | 180000
Fire Protection System | 0 | 11770 | 434040 | 210330 | 202150 | 0 | 858290
HVAC | 0 | 382320 | 247620 | 151630 | 0 | 0 | 781570
Interior | 0 | 919590 | 130440 | 147040 | 0 | 5400 | 1202470
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 5352950 | 5352950
Plumbing System | 0 | 147570 | 52970 | 6870 | 44120 | 299080 | 550610
Roof | 0 | 449230 | 207020 | 84620 | 262230 | 53930 | 1057030
Structural Elements | 0 | 367180 | 0 | 0 | 0 | 45840 | 413020
Structural Upgrade | 0 | 800420 | 3906300 | 3906950 | 940610 | 43140 | 9597420
Vertical Transportation | 0 | 8830 | 0 | 0 | 0 | 0 | 8830
Miscellaneous | 0 | 736090 | 911080 | 970590 | 696550 | 69740 | 3384050
Contingencies | 0 | 586130 | 730430 | 694600 | 227850 | 570380 | 2809390
Preliminaries | 0 | 644750 | 803460 | 764050 | 250630 | 647020 | 3109910
Engineering and Management | 0 | 354480 | 459890 | 421970 | 137920 | 355870 | 1730130
Building Fabric | 1 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 1 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 1 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 1 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 1 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 1 | 94590 | 49570 | 0 | 0 | 0 | 144160
Mechanical System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 1 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 1 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 1 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 1 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 1 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 1 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 1 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 1 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 2 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 2 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 2 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 2 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 2 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 2 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 2 | 12360 | 0 | 0 | 0 | 0 | 12360
Mechanical System | 2 | 7850 | 0 | 0 | 0 | 0 | 7850
Perimeter Fence | 2 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 2 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 2 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 2 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 2 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 2 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 2 | 110270 | 0 | 39480 | 0 | 34320 | 184070
Contingencies | 2 | 7090 | 0 | 0 | 0 | 3440 | 10530
Preliminaries | 2 | 7800 | 0 | 0 | 0 | 3780 | 11580
Engineering and Management | 2 | 4290 | 0 | 0 | 0 | 2080 | 6370
Building Fabric | 3 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 3 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 3 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 3 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 3 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 3 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 3 | 0 | 25020 | 12700 | 0 | 0 | 37720
Mechanical System | 3 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 3 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 3 | 30330 | 0 | 0 | 0 | 0 | 30330
Roof | 3 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 3 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 3 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 3 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 3 | 28680 | 0 | 0 | 0 | 0 | 28680
Contingencies | 3 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 3 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 3 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 4 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 4 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 4 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 4 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 4 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 4 | 0 | 0 | 56370 | 0 | 0 | 56370
Mechanical System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 4 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 4 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 4 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 4 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 4 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 4 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 4 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 4 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 4 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 5 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 5 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 5 | 0 | 0 | 0 | 30000 | 0 | 30000
Fire Protection System | 5 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 5 | 624260 | 871340 | 800970 | 0 | 0 | 2296570
Interior | 5 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 5 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 5 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 5 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 5 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 5 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 5 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 5 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 5 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 5 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 6 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 6 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 6 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 6 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 6 | 43300 | 0 | 0 | 0 | 0 | 43300
Interior | 6 | 1480 | 46760 | 0 | 0 | 0 | 48240
Mechanical System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 6 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 6 | 135700 | 122360 | 0 | 152010 | 0 | 410070
Structural Elements | 6 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 6 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 6 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 6 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 6 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 6 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 6 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 7 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 7 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 7 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 7 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 7 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 7 | 5930 | 0 | 0 | 0 | 0 | 5930
Mechanical System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 7 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 7 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 7 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 7 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 7 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 7 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 7 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 7 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 7 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 8 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 8 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 8 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 8 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 8 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 8 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 8 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 8 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 8 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 8 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 8 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 8 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 8 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 8 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 9 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 9 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 9 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 9 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 9 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 9 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 9 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 9 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 9 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 9 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 9 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 9 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 9 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 9 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 9 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 10 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 10 | 89420 | 828550 | 0 | 0 | 0 | 917970
Electrical System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 10 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 10 | 407610 | 110950 | 5500 | 0 | 0 | 524060
Interior | 10 | 181340 | 66260 | 70160 | 0 | 5400 | 323160
Mechanical System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 10 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 10 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 10 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 10 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 10 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 10 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 10 | 1640 | 82860 | 0 | 0 | 0 | 84500
Preliminaries | 10 | 1810 | 91150 | 0 | 0 | 0 | 92960
Engineering and Management | 10 | 100 | 50130 | 0 | 0 | 0 | 50230
Building Fabric | 11 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 11 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 11 | 356600 | 165620 | 45850 | 210980 | 1610 | 780660
Environmental | 11 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 11 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 11 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 11 | 123320 | 4710 | 0 | 0 | 0 | 128030
Mechanical System | 11 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 11 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 11 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 11 | 0 | 1341400 | 13190 | 89650 | 0 | 1444240
Structural Elements | 11 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 11 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 11 | 88240 | 0 | 0 | 0 | 0 | 88240
Miscellaneous | 11 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 11 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 11 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 11 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 12 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 12 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 12 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 12 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 12 | 12360 | 0 | 0 | 0 | 0 | 12360
Mechanical System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 12 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 12 | 0 | 322240 | 0 | 0 | 0 | 322240
Structural Elements | 12 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 12 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 12 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 12 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 12 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 12 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 12 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 13 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 13 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 13 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 13 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 13 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 13 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 13 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 13 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 13 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 13 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 13 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 13 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 13 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 13 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 13 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 14 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 14 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 14 | 0 | 0 | 7420 | 0 | 0 | 7420
Environmental | 14 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 14 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 14 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 14 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 14 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 14 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 14 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 14 | 0 | 0 | 1488210 | 0 | 0 | 1488210
Structural Elements | 14 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 14 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 14 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 14 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 14 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 14 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 14 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 15 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 15 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 15 | 1985300 | 0 | 0 | 0 | 0 | 1985300
Environmental | 15 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 15 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 15 | 59530 | 936280 | 800970 | 0 | 0 | 1796780
Interior | 15 | 40520 | 0 | 0 | 0 | 0 | 40520
Mechanical System | 15 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 15 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 15 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 15 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 15 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 15 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 15 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 15 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 15 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 15 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 15 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 16 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 16 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 16 | 294120 | 0 | 0 | 0 | 0 | 294120
Environmental | 16 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 16 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 16 | 357030 | 0 | 0 | 0 | 0 | 357030
Interior | 16 | 79350 | 86950 | 12700 | 0 | 0 | 179000
Mechanical System | 16 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 16 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 16 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 16 | 338830 | 0 | 0 | 211770 | 0 | 550600
Structural Elements | 16 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 16 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 16 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 16 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 16 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 16 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 16 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 17 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 17 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 17 | 189020 | 0 | 0 | 0 | 0 | 189020
Environmental | 17 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 17 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 17 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 17 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 17 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 17 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 17 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 17 | 95690 | 0 | 0 | 0 | 0 | 95690
Structural Elements | 17 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 17 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 17 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 17 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 17 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 17 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 17 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 18 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 18 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 18 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 18 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 18 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 18 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 18 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 18 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 18 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 18 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 18 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 18 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 18 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 18 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 18 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 19 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 19 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 19 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 19 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 19 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 19 | 0 | 0 | 56370 | 0 | 0 | 56370
Mechanical System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 19 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 19 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 19 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 19 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 19 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 19 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 19 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 19 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 19 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 20 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 20 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 20 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 20 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 20 | 721350 | 110950 | 5500 | 0 | 0 | 837800
Interior | 20 | 462600 | 66260 | 70160 | 0 | 5400 | 604420
Mechanical System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 20 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 20 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 20 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 20 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 20 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 20 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 20 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 20 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 20 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 21 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 21 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 21 | 70000 | 50190 | 0 | 0 | 0 | 120190
Environmental | 21 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 21 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 21 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 21 | 16720 | 0 | 0 | 0 | 0 | 16720
Mechanical System | 21 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 21 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 21 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 21 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 21 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 21 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 21 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 21 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 21 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 21 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 21 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 22 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 22 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 22 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 22 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 22 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 22 | 18290 | 0 | 0 | 0 | 0 | 18290
Mechanical System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 22 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 22 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 22 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 22 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 22 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 22 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 22 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 22 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 22 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 23 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 23 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 23 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 23 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 23 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 23 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 23 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 23 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 23 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 23 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 23 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 23 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 23 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 23 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 23 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 24 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 24 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 24 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 24 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 24 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 24 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 24 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 24 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 24 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 24 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 24 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 24 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 24 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 24 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 24 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 25 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 25 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 25 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 25 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 25 | 59530 | 882160 | 800970 | 0 | 0 | 1742660
Interior | 25 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 25 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 25 | 1480 | 0 | 0 | 0 | 0 | 1480
Structural Elements | 25 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 25 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 25 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 25 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 25 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 25 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 25 | 0 | 0 | 0 | 0 | 0 | 0
|  | 14087450 | 14721800 | 12130820 | 3558590 | 7528880 | 52027540

## 1-2year
Facilities |  | 1 |  |  |  |  | Total
|  | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 1 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 1 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 1 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 1 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 1 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 1 | 94590 | 49570 | 0 | 0 | 0 | 144160
Mechanical System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 1 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 1 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 1 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 1 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 1 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 1 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 1 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 1 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 1 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 1 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 2 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 2 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 2 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 2 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 2 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 2 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 2 | 12360 | 0 | 0 | 0 | 0 | 12360
Mechanical System | 2 | 7850 | 0 | 0 | 0 | 0 | 7850
Perimeter Fence | 2 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 2 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 2 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 2 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 2 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 2 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 2 | 110270 | 0 | 39480 | 0 | 34320 | 184070
Contingencies | 2 | 7090 | 0 | 0 | 0 | 3440 | 10530
Preliminaries | 2 | 7800 | 0 | 0 | 0 | 3780 | 11580
Engineering and Management | 2 | 4290 | 0 | 0 | 0 | 2080 | 6370
|  | 401120 | 49570 | 39480 | 0 | 43620 | 533790

## 3-5year
Facilities |  | 1 |  |  |  |  | Total
|  | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 3 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 3 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 3 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 3 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 3 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 3 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 3 | 0 | 25020 | 12700 | 0 | 0 | 37720
Mechanical System | 3 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 3 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 3 | 30330 | 0 | 0 | 0 | 0 | 30330
Roof | 3 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 3 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 3 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 3 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 3 | 28680 | 0 | 0 | 0 | 0 | 28680
Contingencies | 3 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 3 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 3 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 4 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 4 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 4 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 4 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 4 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 4 | 0 | 0 | 56370 | 0 | 0 | 56370
Mechanical System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 4 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 4 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 4 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 4 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 4 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 4 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 4 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 4 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 4 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 4 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 5 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 5 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 5 | 0 | 0 | 0 | 30000 | 0 | 30000
Fire Protection System | 5 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 5 | 624260 | 871340 | 800970 | 0 | 0 | 2296570
Interior | 5 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 5 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 5 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 5 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 5 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 5 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 5 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 5 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 5 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 5 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 5 | 0 | 0 | 0 | 0 | 0 | 0
|  | 840140 | 896360 | 870040 | 30000 | 0 | 2636540

## 6-10year
Facilities |  | 1 |  |  |  |  | Total
|  | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 6 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 6 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 6 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 6 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 6 | 43300 | 0 | 0 | 0 | 0 | 43300
Interior | 6 | 1480 | 46760 | 0 | 0 | 0 | 48240
Mechanical System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 6 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 6 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 6 | 135700 | 122360 | 0 | 152010 | 0 | 410070
Structural Elements | 6 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 6 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 6 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 6 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 6 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 6 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 6 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 7 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 7 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 7 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 7 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 7 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 7 | 5930 | 0 | 0 | 0 | 0 | 5930
Mechanical System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 7 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 7 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 7 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 7 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 7 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 7 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 7 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 7 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 7 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 7 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 8 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 8 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 8 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 8 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 8 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 8 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 8 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 8 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 8 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 8 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 8 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 8 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 8 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 8 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 8 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 8 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 9 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 9 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 9 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 9 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 9 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 9 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 9 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 9 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 9 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 9 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 9 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 9 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 9 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 9 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 9 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 9 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 10 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 10 | 89420 | 828550 | 0 | 0 | 0 | 917970
Electrical System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 10 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 10 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 10 | 407610 | 110950 | 5500 | 0 | 0 | 524060
Interior | 10 | 181340 | 66260 | 70160 | 0 | 5400 | 323160
Mechanical System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 10 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 10 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 10 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 10 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 10 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 10 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 10 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 10 | 1640 | 82860 | 0 | 0 | 0 | 84500
Preliminaries | 10 | 1810 | 91150 | 0 | 0 | 0 | 92960
Engineering and Management | 10 | 100 | 50130 | 0 | 0 | 0 | 50230
|  | 868330 | 1399020 | 75660 | 152010 | 5400 | 2500420

## 11-25years
Facilities |  | 1 |  |  |  |  | Total
|  | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 11 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 11 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 11 | 356600 | 165620 | 45850 | 210980 | 1610 | 780660
Environmental | 11 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 11 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 11 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 11 | 123320 | 4710 | 0 | 0 | 0 | 128030
Mechanical System | 11 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 11 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 11 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 11 | 0 | 1341400 | 13190 | 89650 | 0 | 1444240
Structural Elements | 11 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 11 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 11 | 88240 | 0 | 0 | 0 | 0 | 88240
Miscellaneous | 11 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 11 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 11 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 11 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 12 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 12 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 12 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 12 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 12 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 12 | 12360 | 0 | 0 | 0 | 0 | 12360
Mechanical System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 12 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 12 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 12 | 0 | 322240 | 0 | 0 | 0 | 322240
Structural Elements | 12 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 12 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 12 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 12 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 12 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 12 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 12 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 13 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 13 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 13 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 13 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 13 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 13 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 13 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 13 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 13 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 13 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 13 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 13 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 13 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 13 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 13 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 13 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 14 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 14 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 14 | 0 | 0 | 7420 | 0 | 0 | 7420
Environmental | 14 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 14 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 14 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 14 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 14 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 14 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 14 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 14 | 0 | 0 | 1488210 | 0 | 0 | 1488210
Structural Elements | 14 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 14 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 14 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 14 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 14 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 14 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 14 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 15 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 15 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 15 | 1985300 | 0 | 0 | 0 | 0 | 1985300
Environmental | 15 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 15 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 15 | 59530 | 936280 | 800970 | 0 | 0 | 1796780
Interior | 15 | 40520 | 0 | 0 | 0 | 0 | 40520
Mechanical System | 15 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 15 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 15 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 15 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 15 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 15 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 15 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 15 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 15 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 15 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 15 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 16 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 16 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 16 | 294120 | 0 | 0 | 0 | 0 | 294120
Environmental | 16 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 16 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 16 | 357030 | 0 | 0 | 0 | 0 | 357030
Interior | 16 | 79350 | 86950 | 12700 | 0 | 0 | 179000
Mechanical System | 16 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 16 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 16 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 16 | 338830 | 0 | 0 | 211770 | 0 | 550600
Structural Elements | 16 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 16 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 16 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 16 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 16 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 16 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 16 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 17 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 17 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 17 | 189020 | 0 | 0 | 0 | 0 | 189020
Environmental | 17 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 17 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 17 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 17 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 17 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 17 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 17 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 17 | 95690 | 0 | 0 | 0 | 0 | 95690
Structural Elements | 17 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 17 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 17 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 17 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 17 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 17 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 17 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 18 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 18 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 18 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 18 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 18 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 18 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 18 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 18 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 18 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 18 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 18 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 18 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 18 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 18 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 18 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 18 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 19 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 19 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 19 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 19 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 19 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 19 | 0 | 0 | 56370 | 0 | 0 | 56370
Mechanical System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 19 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 19 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 19 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 19 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 19 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 19 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 19 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 19 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 19 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 19 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 20 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 20 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 20 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 20 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 20 | 721350 | 110950 | 5500 | 0 | 0 | 837800
Interior | 20 | 462600 | 66260 | 70160 | 0 | 5400 | 604420
Mechanical System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 20 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 20 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 20 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 20 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 20 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 20 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 20 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 20 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 20 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 20 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 21 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 21 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 21 | 70000 | 50190 | 0 | 0 | 0 | 120190
Environmental | 21 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 21 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 21 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 21 | 16720 | 0 | 0 | 0 | 0 | 16720
Mechanical System | 21 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 21 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 21 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 21 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 21 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 21 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 21 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 21 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 21 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 21 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 21 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 22 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 22 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 22 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 22 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 22 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 22 | 18290 | 0 | 0 | 0 | 0 | 18290
Mechanical System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 22 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 22 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 22 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 22 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 22 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 22 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 22 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 22 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 22 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 22 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 23 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 23 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 23 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 23 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 23 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 23 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 23 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 23 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 23 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 23 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 23 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 23 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 23 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 23 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 23 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 23 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 24 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 24 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 24 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 24 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 24 | 0 | 0 | 0 | 0 | 0 | 0
Interior | 24 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 24 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 24 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 24 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 24 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 24 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 24 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 24 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 24 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 24 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 24 | 0 | 0 | 0 | 0 | 0 | 0
Building Fabric | 25 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 25 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 25 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 25 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 25 | 59530 | 882160 | 800970 | 0 | 0 | 1742660
Interior | 25 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 25 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 25 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 25 | 1480 | 0 | 0 | 0 | 0 | 1480
Structural Elements | 25 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 25 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 25 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 25 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 25 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 25 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 25 | 0 | 0 | 0 | 0 | 0 | 0
|  | 5683620 | 3966760 | 3301340 | 512400 | 7010 | 13471130

## Data
Technical and Environmental Due Diligence of Hanjin Shipyard
for Cerberus Capital Management
CAPEX Optimization of Facilities - Phase 2 | [20 empty] | 0
As of March 30, 2020 | [32 empty] | 50190
Facilities | User | Area | 0 |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  | 25
|  |  | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2 | Phase 1 | Phase 2
Air Compressed Room - 1 | Dock 6 | 1342 | 33320 | 50810 | 0 | 0 | 0 | 39480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Compressed Room - 2,3 | Austal | 382 | 95200 | 19050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50190 | 50190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly shelter (6 nos) | Austal | 11130 | 773610 | 427030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly shop (A) | Austal | 27390 | 537350 | 888260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151060 | 322240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly shop (B) | Austal | 40562 | 1170090 | 1333770 | 0 | 0 | 143700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318770 | 318140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly Shop (C) | Dock 6 | 27025 | 779570 | 628680 | 0 | 0 | 635900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36400 | 0 | 0 | 0 | 0 | 0 | 129930 | 529910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly Shop (D) | Navy | 11880 | 342700 | 166820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57120 | 129420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16030 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - Accommodation | Navy | 166 | 0 | 4740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - Admin | Navy | 1500 | 0 | 128120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - B | Navy | 780 | 0 | 97960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 489000 | 73980 | 6790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - C | Navy | 1300 | 0 | 207840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - D | Navy | 1050 | 0 | 156410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - E | Navy | 1300 | 0 | 150950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - F | Navy | 700 | 0 | 43620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - G1 | Navy | 1100 | 0 | 108830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - G2 | Navy | 1500 | 0 | 120050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - J | Navy | 210 | 0 | 13100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - K | Navy | 2600 | 0 | 64790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barracks - Romanian | Navy | 210 | 0 | 13100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blasting & Painting Shop B | Austal | 13895 | 1001900 | 398930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blasting & Painting Shop C | Dock 6 | 15001 | 1031330 | 411100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20230 | 20230 | 0 | 0 | 0 | 0 | 721160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blasting & Painting Shop D | Dock 6 | 15008 | 1031500 | 411290 | 0 | 0 | 353117.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20230 | 20230 | 0 | 0 | 0 | 0 | 721160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blasting & Painting Shop E | Navy | 5913 | 170570 | 66690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blasting Shop A | Dock 6 | 5485 | 158230 | 151220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 0 | 0 | 0 | 0 | 0 | 0 | 7420 | 7420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 Plant | Navy | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cable Cutting | Navy | 1250 | 0 | 155300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2730 | 150000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Canteen-Romanian | Navy | 220 | 0 | 0 | 0 | 0 | 0 | 27420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Catering Center | Navy | 6186 | 249500 | 420740 | 74900 | 89500 | 0 | 156870 | 83800 | 30330 | 0 | 156870 | 993200 | 156870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130390 | 0 | 16450 | 33170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72780 | 0 | 156870 | 0 | 0 | 0 | 156870 | 0 | 156870 | 0 | 16720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Convenience Store building | Navy | 502 | 0 | 0 | 0 | 0 | 63100 | 62550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dhouse Shelter | Tenant 3 | 15180 | 472190 | 613050 | 0 | 0 | 638200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36540 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric Steel Outfitting Shop | Navy | 3300 | 341030 | 394630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2730 | 85690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric Steel Outfitting Shop (Building at the back) | Navy | 1000 | 230500 | 178650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1480
Field Office 1 | Austal | 1346 | 11700 | 239400 | 0 | 0 | 42000 | 0 | 0 | 15840 | 0 | 0 | 0 | 184000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184000 | 0 | 15840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184000
Field Office 10 | Dock 6 | 1079 | 8900 | 198070 | 0 | 0 | 32100 | 0 | 0 | 12700 | 0 | 0 | 0 | 146120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146120 | 0 | 12700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146120
Field Office 11A | Dock 6 | 845 | 10000 | 214580 | 0 | 0 | 36100 | 0 | 0 | 0 | 0 | 9950 | 0 | 116360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9950 | 0 | 4280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116360
Field Office 11B | Dock 6 | 1300 | 11800 | 327880 | 0 | 0 | 42400 | 0 | 0 | 0 | 0 | 15300 | 0 | 175890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15300 | 0 | 7360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175890
Field Office 12 | Dock 6 | 785 | 12500 | 149200 | 0 | 0 | 45200 | 0 | 0 | 0 | 0 | 9240 | 0 | 108240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9240 | 0 | 14020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108240
Field Office 13 | Navy | 300 | 5200 | 72090 | 0 | 0 | 18500 | 12360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5930 | 0 | 0 | 0 | 0 | 0 | 10460 | 0 | 0 | 0 | 12360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10460 | 0 | 0 | 0 | 18290 | 0 | 0 | 0 | 0 | 0 | 0
Field Office 14 | Navy | 310 | 5200 | 27560 | 0 | 0 | 18500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1830 | 0 | 3650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Field Office 15 | Austal | 400 | 5200 | 71860 | 0 | 0 | 18500 | 0 | 0 | 0 | 0 | 0 | 0 | 54120 | 0 | 12360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54120 | 0 | 12360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Field Office 2 | Austal | 640 | 7500 | 208090 | 0 | 8480 | 27000 | 0 | 0 | 0 | 0 | 0 | 0 | 97420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97420 | 0 | 8480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97420
Field Office 2A | Austal | 720 | 8500 | 210030 | 0 | 8480 | 30500 | 0 | 0 | 0 | 0 | 0 | 0 | 97420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97420 | 0 | 8480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97420
Field Office 3 | Austal | 432 | 5200 | 111720 | 0 | 5090 | 18500 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 0 | 5090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530
Field Office 5 | Navy | 432 | 5200 | 71210 | 0 | 5090 | 18500 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 0 | 5090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530
Field Office 5A | Dock 6 | 594 | 7100 | 100290 | 0 | 0 | 25400 | 0 | 0 | 0 | 0 | 6990 | 0 | 81180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6990 | 0 | 4720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81180
Field Office 6 | Austal | 780 | 6100 | 144050 | 0 | 0 | 9600 | 0 | 0 | 9180 | 0 | 0 | 0 | 105530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105530 | 0 | 9180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105530
Field Office 6a | Austal | 630 | 22000 | 163240 | 0 | 9530 | 34700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Field Office 7 | Austal | 575 | 6800 | 100590 | 0 | 6770 | 24500 | 0 | 0 | 0 | 0 | 0 | 0 | 78480 | 0 | 8460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78480 | 0 | 6770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78480
Field Office 8 | Austal | 953 | 7500 | 233080 | 0 | 11220 | 27000 | 0 | 0 | 0 | 0 | 0 | 0 | 194840 | 0 | 14020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259780 | 0 | 11220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259780
Field Office 9 | Dock 6 | 1265 | 12100 | 232170 | 0 | 0 | 43500 | 0 | 0 | 0 | 0 | 14890 | 0 | 173180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14890 | 0 | 19420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173180
Filtration Plant | Shared | 350 | 0 | 0 | 0 | 0 | 8900 | 43620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Station | Dock 6 | 225 | 0 | 31230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gasoline Station | Navy | 300 | 0 | 37400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Guest House | Navy | 2610 | 855570 | 645320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6180 | 3920 | 3920 | 0 | 0 | 0 | 0 | 0 | 0 | 101400 | 40520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466700 | 163050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hatch cover Shelter | Tenant 3 | 16000 | 935300 | 784280 | 0 | 0 | 744500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49840 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Helicopter Hangar | Navy | 900 | 0 | 56080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hull Shop (A) | Austal | 37736 | 1291740 | 1199130 | 0 | 0 | 780400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320570 | 443960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hull Shop B | Dock 6 | 38920 | 342960 | 1169510 | 0 | 0 | 744500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123760 | 0 | 0 | 0 | 0 | 0 | 160170 | 152630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main Gate | Navy | 1342 | 39470 | 50810 | 0 | 0 | 0 | 39480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main Generator Room | Navy | 1000 | 0 | 1900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1985300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main Office | Navy | 15000 | 455900 | 1398200 | 0 | 0 | 0 | 0 | 11600 | 28680 | 0 | 0 | 1952000 | 250990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44120 | 12600 | 203790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintenance Shop | Dock 6 | 1500 | 43120 | 41130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Material Store and Bond shop | Tenant 3 | 9500 | 0 | 6250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Outfitting Shop A | Tenant 3 | 3950 | 0 | 246020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Procurement Storage shop | Tenant 3 | 2100 | 0 | 26170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Segragation Area | Tenant 3 | 2500 | 0 | 31160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Stock office | Tenant 3 | 60 | 0 | 7490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Stock Room 1 | Tenant 3 | 360 | 0 | 44860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Stock Room 2 | Tenant 3 | 300 | 0 | 37400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nagyantok Warehouse | Tenant 3 | 650 | 0 | 28370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No.5 Dock Shelter | Austal | 4950 | 172700 | 184980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49840 | 82550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outfitting Shop | Austal | 5600 | 0 | 217660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Paint Can Stock Area | Dock 6 | 1550 | 112570 | 42500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Painting Shop A -1 | Navy | 860 | 0 | 29820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Painting Shop A Ext. | Dock 6 | 10500 | 386990 | 287760 | 0 | 0 | 253100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Panel Shop | Dock 6 | 54983 | 1586040 | 1536870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74060 | 0 | 0 | 0 | 0 | 0 | 2643400 | 539050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pipe Manufacture Shop A&B | Navy | 10462 | 905370 | 181270 | 0 | 0 | 246165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14140 | 140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Piping Pre-treatment building Galva | Navy | 2900 | 1137325 | 1021720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145600 | 0
Piping Shelter | Navy | 1000 | 0 | 14100 | 0 | 0 | 0 | 7850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Powerplant and Control Station | Shared | 1100 | 154340 | 207280 | 0 | 0 | 0 | 0 | 58500 | 0 | 0 | 0 | 58500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 1610 | 1610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre Treatment Shop A | Austal | 4662 | 92015 | 127790 | 0 | 0 | 68600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4305 | 18290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre Treatment Shop B | Austal | 3362 | 92015 | 92160 | 0 | 0 | 68600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4305 | 13190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | Dock 6 | 18983 | 168920 | 605440 | 0 | 0 | 649200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37170 | 0 | 0 | 0 | 0 | 0 | 24520 | 74450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-erection area (6 nos) - No. 5 Dock Shelter | Austal | 17220 | 349320 | 582970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13790 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-Outfitting Shop (A) | Austal | 8805 | 254000 | 266880 | 0 | 0 | 143700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19600 | 69060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-Outfitting Shop (B) | Dock 6 | 5734 | 164770 | 174450 | 0 | 0 | 134400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32220 | 67460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Production Center 1/Hospital Building/Substation 8 | Austal | 10564 | 4255220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1077500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Samandra - Container Shop | Tenant 3 | 1542 | 0 | 28670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Samandra - Maintenance Shop/Office | Tenant 3 | 1650 | 0 | 192080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Samandra - Shop B | Tenant 3 | 2300 | 0 | 6250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Samandra - Warehouse | Tenant 3 | 2301 | 0 | 20580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sewage Treatment Plant | Shared | 1120 | 0 | 296250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shared Utilities - Electricity | Shared | 0 | 0 | 37500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shared Utilities - Water | Shared | 0 | 0 | 130880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shared Utilities - Fence | Shared | 0 | 0 | 6800940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shelter 712 | Navy | 1100 | 0 | 41120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12700 | 6280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shelter for Piping | Navy | 2090 | 519500 | 22940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94290 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slope protection | Tenant 3 | 0 | 50000 | 78010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spill Prevention Kits/Secondary Containment Tenant 3 | Tenant 3 | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spill Prevention Kits/Secondary Containment Austal | Austal | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spill Prevention Kits/Secondary Containment Dock 6 | Dock 6 | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spill Prevention Kits/Secondary Containment Navy | Navy | 0 | 32500 | 45450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Steel Stock Yard | Dock 6 | 37275 | 0 | 92880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Assembly Shop | Austal | 15560 | 378400 | 537410 | 0 | 0 | 143700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80780 | 122040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #10 | Dock 6 | 207 | 0 | 26370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #11 | Austal | 800 | 0 | 44870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #12 | Austal | 735 | 0 | 67410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #13 | Austal | 371 | 0 | 40220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #14 | Austal | 612 | 0 | 58220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #15 | Austal | 332 | 0 | 37290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #16 | Austal | 360 | 0 | 30170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #17 | Austal | 460 | 0 | 46860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #20 | Austal | 325 | 0 | 36780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #21 | Dock 6 | 1300 | 0 | 44870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #22 | Dock 6 | 760 | 0 | 69280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #22-1 | Dock 6 | 685 | 0 | 29550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #23 | Dock 6 | 410 | 0 | 22700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #24 | Dock 6 | 340 | 0 | 20950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #25 | Dock 6 | 325 | 0 | 36780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub station #26 | Dock 6 | 760 | 0 | 69280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #3 | Austal | 390 | 0 | 30930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #30 | Dock 6 | 890 | 0 | 34650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #31 | Navy | 320 | 0 | 36400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #32 | Dock 6 | 800 | 0 | 72270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #33 | Navy | 685 | 0 | 29550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #34 | Dock 6 | 260 | 0 | 18960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #35 | Navy | 260 | 0 | 18960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #36 | Tenant 3 | 400 | 0 | 42370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #37 | Austal | 250 | 0 | 20560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #38 | Tenant 3 | 270 | 0 | 32660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub Station #9 | Austal | 360 | 0 | 39380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sub-Assembly Shop (94 bay) | Tenant 3 | 10800 | 311540 | 207970 | 0 | 0 | 254200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14560 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T-BHD Shelter | Tenant 3 | 11430 | 678710 | 385090 | 0 | 0 | 540300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141330 | 89650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tool Shop | Austal | 985 | 0 | 36830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waste Matter/Scrap Iron Stock | Dock 6 | 986 | 0 | 97180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Welding Inspection Shop | Austal | 5000 | 138470 | 143270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Welding Shop (B) | Dock 6 | 10600 | 329870 | 372720 | 0 | 0 | 269490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70360 | 124710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 646597 | 24909235 | 32885660 | 74900 | 144160 | 7396272.65 | 389630 | 153900 | 96730 | 0 | 213240 | 4111200 | 2326570 | 354100 | 501610 | 0 | 5930 | 0 | 0 | 0 | 0 | 619390 | 1992880 | 1522250 | 2441170 | 151060 | 334600 | 0 | 0 | 5169790 | 1495630 | 101400 | 3822600 | 0 | 1380750 | 5460 | 441580 | 0 | 0 | 0 | 213240 | 466700 | 1442220 | 66220 | 136910 | 0 | 18290 | 0 | 0 | 0 | 0 | 145600 | 1744140
Distribution of Works per year
Facilities | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Building Fabric | 138830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 1711160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780660 | 0 | 0 | 7420 | 1985300 | 294120 | 189020 | 0 | 0 | 0 | 120190 | 0 | 0 | 0 | 0
Environmental | 180000 | 0 | 0 | 0 | 0 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 858290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 781570 | 0 | 156870 | 0 | 156870 | 2296570 | 43300 | 0 | 0 | 0 | 524060 | 0 | 0 | 0 | 0 | 1796780 | 357030 | 156870 | 0 | 156870 | 837800 | 0 | 0 | 0 | 0 | 1742660
Interior | 1202470 | 144160 | 12360 | 37720 | 56370 | 0 | 48240 | 5930 | 0 | 0 | 323160 | 128030 | 12360 | 0 | 0 | 40520 | 179000 | 0 | 0 | 56370 | 604420 | 16720 | 18290 | 0 | 0 | 0
Mechanical System | 0 | 0 | 7850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 5352950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 550610 | 0 | 0 | 30330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 1057030 | 0 | 0 | 0 | 0 | 0 | 410070 | 0 | 0 | 0 | 0 | 1444240 | 322240 | 0 | 1488210 | 0 | 550600 | 95690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1480
Structural Elements | 413020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 9597420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 8830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 3384050 | 0 | 184070 | 28680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 2809390 | 0 | 10530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 3109910 | 0 | 11580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 1730130 | 0 | 6370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 32885660 | 144160 | 389630 | 96730 | 213240 | 2326570 | 501610 | 5930 | 0 | 0 | 1992880 | 2441170 | 334600 | 0 | 1495630 | 3822600 | 1380750 | 441580 | 0 | 213240 | 1442220 | 136910 | 18290 | 0 | 0 | 1744140
| Austal | Dock 6 | Shared | Navy | Tenant 3
Facilities | Air Compressed Room - 2,3 | Air Compressed Room - 1 | Filtration Plant | Assembly Shop (D) | Dhouse Shelter
| Assembly shelter (6 nos) | Assembly Shop (C) | Powerplant and Control Station | Barracks - Accommodation | Hatch cover Shelter
| Assembly shop (A) | Blasting & Painting Shop C | Sewage Treatment Plant | Barracks - Admin | Nagyantok Material Store and Bond shop
| Assembly shop (B) | Blasting & Painting Shop D | Shared Utilities - Electricity | Barracks - B | Nagyantok Outfitting Shop A
| Blasting & Painting Shop B | Blasting Shop A | Shared Utilities - Water | Barracks - C | Nagyantok Procurement Storage shop
| Field Office 1 | Field Office 10 | Shared Utilities - Fence | Barracks - D | Nagyantok Segragation Area
| Field Office 15 | Field Office 11A |  | Barracks - E | Nagyantok Stock office
| Field Office 2 | Field Office 11B |  | Barracks - F | Nagyantok Stock Room 1
| Field Office 2A | Field Office 12 |  | Barracks - G1 | Nagyantok Stock Room 2
| Field Office 3 | Field Office 5A |  | Barracks - G2 | Nagyantok Warehouse
| Field Office 6 | Field Office 9 |  | Barracks - J | Samandra - Container Shop
| Field Office 6a | Fire Station |  | Barracks - K | Samandra - Maintenance Shop/Office
| Field Office 7 | Hull Shop B |  | Barracks - Romanian | Samandra - Shop B
| Field Office 8 | Maintenance Shop |  | Blasting & Painting Shop E | Samandra - Warehouse
| Hull Shop (A) | Paint Can Stock Area |  | CO2 Plant | Slope protection
| No.5 Dock Shelter | Painting Shop A Ext. |  | Cable Cutting | Spill Prevention Kits/Secondary Containment Tenant 3
| Outfitting Shop | Panel Shop |  | Canteen-Romanian | Sub Station #36
| Pre Treatment Shop A | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) |  | Catering Center | Sub Station #38
| Pre Treatment Shop B | Pre-Outfitting Shop (B) |  | Convenience Store building | Sub-Assembly Shop (94 bay)
| Pre-erection area (6 nos) - No. 5 Dock Shelter | Steel Stock Yard |  | Electric Steel Outfitting Shop | T-BHD Shelter
| Pre-Outfitting Shop (A) | Sub Station #10 |  | Electric Steel Outfitting Shop (Building at the back)
| Production Center 1/Hospital Building/Substation 8 | Sub station #21 |  | Field Office 13
| Sub Assembly Shop | Sub station #22 |  | Field Office 14
| Sub station #11 | Sub station #22-1 |  | Field Office 5
| Sub station #12 | Sub Station #23 |  | Gasoline Station
| Sub Station #13 | Sub Station #24 |  | Guest House
| Sub Station #14 | Sub station #25 |  | Helicopter Hangar
| Sub Station #15 | Sub station #26 |  | Main Gate
| Sub Station #16 | Sub Station #30 |  | Main Generator Room
| Sub station #17 | Sub Station #32 |  | Main Office
| Sub station #20 | Sub Station #34 |  | Painting Shop A -1
| Sub Station #3 | Waste Matter/Scrap Iron Stock |  | Pipe Manufacture Shop A&B
| Sub Station #37 | Welding Shop (B) |  | Piping Pre-treatment building Galva
| Sub Station #9 |  |  | Piping Shelter
| Tool Shop |  |  | Shelter 712
| Welding Inspection Shop |  |  | Shelter for Piping
Spill Prevention Kits/Secondary Containment Navy
Sub Station #31
Sub Station #33
Sub Station #35
Building work type distribution per tenant per year
Facilities | 0 |  |  |  |  | Total
| Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 138830 | 0 | 0 | 0 | 0 | 138830
Demolition | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 714550 | 494340 | 453150 | 19620 | 29500 | 1711160
Environmental | 32500 | 32500 | 32500 | 82500 | 0 | 180000
Fire Protection System | 11770 | 434040 | 210330 | 202150 | 0 | 858290
HVAC | 382320 | 247620 | 151630 | 0 | 0 | 781570
Interior | 919590 | 130440 | 147040 | 0 | 5400 | 1202470
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 5352950 | 5352950
Plumbing System | 147570 | 52970 | 6870 | 44120 | 299080 | 550610
Roof | 449230 | 207020 | 84620 | 262230 | 53930 | 1057030
Structural Elements | 367180 | 0 | 0 | 0 | 45840 | 413020
Structural Upgrade | 800420 | 3906300 | 3906950 | 940610 | 43140 | 9597420
Vertical Transportation | 8830 | 0 | 0 | 0 | 0 | 8830
Miscellaneous | 736090 | 911080 | 970590 | 696550 | 69740 | 3384050
Contingencies | 586130 | 730430 | 694600 | 227850 | 570380 | 2809390
Preliminaries | 644750 | 803460 | 764050 | 250630 | 647020 | 3109910
Engineering and Management | 354480 | 459890 | 421970 | 137920 | 355870 | 1730130
Total | 6294240 | 8410090 | 7844300 | 2864180 | 7472850 | 32885660
Facilities | 1 |  |  |  |  | 2 |  |  |  |  | Total
| Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 0 | 0 | 0 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 156870
Interior | 94590 | 49570 | 0 | 0 | 0 | 12360 | 0 | 0 | 0 | 0 | 156520
Mechanical System | 0 | 0 | 0 | 0 | 0 | 7850 | 0 | 0 | 0 | 0 | 7850
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 0 | 0 | 0 | 0 | 0 | 110270 | 0 | 39480 | 0 | 34320 | 184070
Contingencies | 0 | 0 | 0 | 0 | 0 | 7090 | 0 | 0 | 0 | 3440 | 10530
Preliminaries | 0 | 0 | 0 | 0 | 0 | 7800 | 0 | 0 | 0 | 3780 | 11580
Engineering and Management | 0 | 0 | 0 | 0 | 0 | 4290 | 0 | 0 | 0 | 2080 | 6370
| 94590 | 49570 | 0 | 0 | 0 | 306530 | 0 | 39480 | 0 | 43620 | 533790
Facilities | 3 |  |  |  |  | 4 |  |  |  |  | 5 |  |  |  |  | Total
| Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30000 | 0 | 30000
Fire Protection System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 0 | 0 | 0 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 624260 | 871340 | 800970 | 0 | 0 | 2453440
Interior | 0 | 25020 | 12700 | 0 | 0 | 0 | 0 | 56370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94090
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 30330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30330
Roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 28680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28680
Contingencies | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 59010 | 25020 | 12700 | 0 | 0 | 156870 | 0 | 56370 | 0 | 0 | 624260 | 871340 | 800970 | 30000 | 0 | 2636540
Facilities | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | Total
| Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89420 | 0 | 0 | 0 | 0 | 89420
Electrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Environmental | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 43300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407610 | 0 | 0 | 0 | 0 | 450910
Interior | 1480 | 46760 | 0 | 0 | 0 | 5930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181340 | 0 | 0 | 0 | 0 | 235510
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 135700 | 122360 | 0 | 152010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410070
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1640 | 0 | 0 | 0 | 0 | 1640
Preliminaries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1810 | 0 | 0 | 0 | 0 | 1810
Engineering and Management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100
| 180480 | 169120 | 0 | 152010 | 0 | 5930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 681920 | 0 | 0 | 0 | 0 | 1189460
Facilities | 11 |  |  |  |  | 12 |  |  |  |  | 13 |  |  |  |  | 14 |  |  |  |  | 15 |  |  |  |  | 16 |  |  |  |  | 17 |  |  |  |  | 18 |  |  |  |  | 19 |  |  |  |  | 20 |  |  |  |  | 21 |  |  |  |  | 22 |  |  |  |  | 23 |  |  |  |  | 24 |  |  |  |  | 25 |  |  |  |  | Total
| Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared | Navy | Austal | Dock 6 | Tenant 3 | Shared
Building Fabric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demolition | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical System | 356600 | 165620 | 45850 | 210980 | 1610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7420 | 0 | 0 | 1985300 | 0 | 0 | 0 | 0 | 294120 | 0 | 0 | 0 | 0 | 189020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70000 | 50190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120190
Environmental | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fire Protection System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 936280 | 800970 | 0 | 0 | 357030 | 0 | 0 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156870 | 0 | 0 | 0 | 0 | 721350 | 110950 | 5500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59530 | 882160 | 800970 | 0 | 0 | 1742660
Interior | 123320 | 4710 | 0 | 0 | 0 | 12360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40520 | 0 | 0 | 0 | 0 | 79350 | 86950 | 12700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56370 | 0 | 0 | 462600 | 66260 | 70160 | 0 | 5400 | 16720 | 0 | 0 | 0 | 0 | 18290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35010
Mechanical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Perimeter Fence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plumbing System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof | 0 | 1341400 | 13190 | 89650 | 0 | 0 | 322240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1488210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338830 | 0 | 0 | 211770 | 0 | 95690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1480 | 0 | 0 | 0 | 0 | 1480
Structural Elements | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Structural Upgrade | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vertical Transportation | 88240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Miscellaneous | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contingencies | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preliminaries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engineering and Management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 568160 | 1511730 | 59040 | 300630 | 1610 | 12360 | 322240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1495630 | 0 | 0 | 2085350 | 936280 | 800970 | 0 | 0 | 1069330 | 86950 | 12700 | 211770 | 0 | 441580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156870 | 0 | 56370 | 0 | 0 | 1183950 | 177210 | 75660 | 0 | 5400 | 86720 | 50190 | 0 | 0 | 0 | 18290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61010 | 882160 | 800970 | 0 | 0 | 13471130

## CAPEX
No | Asset Intervention | Facilities | Floor Level | Area | Tenant | Type of Work | Disciplines | User | Year Built | Arcadis Quantity | Tenant Quantity | Unit | Condition State | Risk | Code Compliance (Yes = 1, No = 0) | Intervention Type | Intervention Percentage | Unit Cost (PHP) | life expectancy | Probabilty of Intervention | Arcadis Intervention Year | Tenant Intervention Year | Phase 1 Included (Yes=1, No=0) | Phase 1 Capex if Included (USD) | Phase 2 CaPex (PHP) | Phase 2 CaPex (USD) | Building Requirements | Reasons for Intervention | Scope of Work for the Reason of Intervention | Photo Reference No. | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
No | CAPEXassets | Facilities | FloorLevel | Area | Tenant | WorkType | Disciplines | User | YearBuilt | Quantity | TenantQ | Unit | States | Risk | CodeComply | InteType | IntePec | UnitCost | LifeSpan | Prob | InterYear | TenantInterYear | IncludedPhase1 | NPVCAPEXP1USD | NPVCapexP2Php | NPVCapexUSD | ReturntoAs-built | ReasonsforIntervention | Scopes | PictureReferenceCode | Remarks
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 |  | 126000 | 2480 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and delapidated | -Re-application of Rubberized flooring to as-built condition
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 1 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 |  | 126000 | 2480 | 1 | - Rubberized paint of the 1st floor is already peeled-off and delapidated | -Re-application of Rubberized flooring to as-built condition
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 2 |  | 1 | 18500 | 315000 | 6180 | 0 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 12 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 22 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 2 |  | 0 | 0 | 315000 | 6180 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 12 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 22 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 3 | 1 | 5 | 0.2 | 720 | 15 | 1 | 0 |  | 0 |  | 60480 | 1190 | 1 | - sections of the ceiling boards are damaged and sagging | - Replacement of new ceiling board to retain its as-built condition
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 5 | 1 | 720 | 15 | 1 | 7 |  | 0 |  | 302400 | 5930 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards due to life expectancy
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 720 | 15 | 1 | 22 |  | 0 |  | 302400 | 5930 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards due to life expectancy
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 4 | 3 | 1 | 5 | 1 | 140000 | 10 | 1 | 0 |  | 0 |  | 280000 | 5500 | 1 | - According to the operator of this field office, the floor mounted AC is not in good condition. - Needs to be checked and tested since it is not operated after the shipyard operation | - Option to replace the floor mounted AC's if found these cannot be repaired.
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 10 |  | 0 |  | 280000 | 5500 | 1 | - life expectancy of HVAC | - Installation of new Air-condition units due to life expectancy
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 20 |  | 0 |  | 280000 | 5500 | 1 | - life expectancy of HVAC | - Installation of new Air-condition units due to life expectancy
7 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 13 | 2 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 6 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 420000 | 8240 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
8 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 13 | 2 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 6 | 1 | 2000 | 25 | 1 | 0 |  | 0 |  | 840000 | 16480 | 2 | - All auxiliary wires are in fair condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
9 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 40 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 80000 | 1570 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
10 | Repair of roofs and gutters | Field Office 13 | Lot | NY | Navy | Roof | Roof | Navy | 2012 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 1 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
11 | Provision for the storm drainage | Field Office 13 | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2012 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 3500 | 0 | 1 | 0 |  | 0 | 0 | 525000 | 10300 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
12 | Miscellaneous items | Field Office 13 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 308748 | 0 | 1 | 0 |  | 0 | 0 | 308748 | 6060 | 1 | - Allocation for the unforeseen repair/installation such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace
13 | Contingencies (10%) | Field Office 13 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 339700 | 0 | 1 | 0 |  | 0 | 0 | 339700 | 6670 | 1 | - Contingencies | 10% contingencies
14 | Preliminaries (10%) | Field Office 13 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 373600 | 0 | 1 | 0 |  | 0 | 0 | 373600 | 7330 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
15 | Permitting and Engineering (5%) | Field Office 13 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192900 | 0 | 1 | 0 |  | 0 | 0 | 192900 | 3790 | 1 | - Soft Cost | - Permitting and Engineering
16 | Panel Boards | Sub Station #33 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
17 | Transformers repair | Sub Station #33 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
18 | Overall Repair of the facility | Sub Station #33 | 1 | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 685 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 685000 | 13440 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
19 | Contingencies (10%) | Sub Station #33 | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 118500 | 0 | 1 | 0 |  | 0 | 0 | 118500 | 2330 | 1 | - Contingencies | 10% contingencies
20 | Preliminaries (10%) | Sub Station #33 | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 130400 | 0 | 1 | 0 |  | 0 | 0 | 130400 | 2560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
21 | Permitting and Engineering (5%) | Sub Station #33 | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 71700 | 0 | 1 | 0 |  | 0 | 0 | 71700 | 1410 | 1 | - Soft Cost | - Permitting and Engineering
22 | Installation of missing X- Brace | Pipe Manufacture Shop A&B | 1 | NY | Navy | Structural Elements | Structural | Navy | 2011 | 313860 |  | kg | 4 | 3 | 1 | 5 | 0.03 | 200 | 0 | 1 | 0 |  | 0 | 0 | 1883160 | 36930 | 1 | - some cross braces are already missing and already experiencing buckling and sagging | - Repair and installation of replacement of X-Braces
23 | Panel Boards | Pipe Manufacture Shop A&B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 721140 | 25 | 0 | 11 |  | 1 | 14140 | 0 | 0 | 1 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
24 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Pipe Manufacture Shop A&B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 70000 | 25 | 1 | 11 |  | 0 | 0 | 7140000 | 140000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
25 | Replacement of polycarbornate Roof | Pipe Manufacture Shop A&B | 1 | NY | Navy | Roof | Roof | Navy | 2011 | 8640 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 16 |  | 0 | 0 | 17280000 | 338830 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
26 | Upgrade to comply current structural code | Pipe Manufacture Shop A&B | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2011 | 10462 |  | m2 | 3 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.1 | 0 |  | 1 | 905370 | 4184800 | 82060 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
27 | Gas port/ Electrical Panel Location Provision of Barricade | Pipe Manufacture Shop A&B | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2011 | 1 |  | lot | 3 | 3 | 1 | 6 | 1 | 600000 | 25 | 0 | 2 |  | 1 | 246165 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
27 | Gas port/ Electrical Panel Location Provision of Barricade | Pipe Manufacture Shop A&B | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2011 | 1 |  | lot | 3 | 3 | 1 | 6 | 1 | 600000 | 25 | 1 | 0 |  | 1 |  | 600000 | 11770 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
28 | Miscellaneous Items | Pipe Manufacture Shop A&B | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 606800 | 0 | 1 | 0 |  | 0 | 0 | 606800 | 11900 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
29 | Contingencies (10%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 727500 | 0 | 1 | 0 |  | 0 | 0 | 727500 | 14270 | 1 | - Contingencies | 10% contingencies
30 | Preliminaries (10%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 800300 | 0 | 1 | 0 |  | 0 | 0 | 800300 | 15700 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
31 | Permitting and Engineering (5%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 440200 | 0 | 1 | 0 |  | 0 | 0 | 440200 | 8640 | 1 | - Soft Cost | - Permitting and Engineering
32 | Panel Boards | Shelter for Piping | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 4808790 | 25 | 0 | 11 |  | 1 | 94290 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
33 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Shelter for Piping | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 0 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
34 | Fire Suppression System | Shelter for Piping | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 12217050 | 0 | 0 | 0 |  | 1 | 239500 | 0 | 0 | 0 | - During our detailed inspection,this building is only for the storage of pipe and other appurtenences. Hence, current fire extinguishing set-up is okay | - No Capex will be allocated to Phase 2
35 | Repair of deformed Structural steel frame | Shelter for Piping | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 1 |  | lot | 4 | 3 | 1 | 3 | 1 | 5793600 | 0 | 0 | 0 |  | 1 | 113600 | 0 | 0 | 0 | - During our detailed inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
36 | Upgrade to comply current structural code | Shelter for Piping | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 2090 |  | m2 | 3 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.1 | 0 |  | 1 | 166400 | 836000 | 16400 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
37 | Miscellaneous Items | Shelter for Piping | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - repainting of rusted structural steel members - poor condition of electrical wires | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Repair/Installation of missing cross braces - Replacement of dilapidated electrical wrings - Repainting of rusted structural member frames
38 | Contingencies (10%) | Shelter for Piping | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92000 | 0 | 1 | 0 |  | 0 | 0 | 92000 | 1810 | 1 | - Contingencies | 10% contingencies
39 | Preliminaries (10%) | Shelter for Piping | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 101200 | 0 | 1 | 0 |  | 0 | 0 | 101200 | 1990 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
40 | Permitting and Engineering (5%) | Shelter for Piping | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 55700 | 0 | 1 | 0 |  | 0 | 0 | 55700 | 1100 | 1 | - Soft Cost | - Permitting and Engineering
41 | Demolition and Debris Removal of CO2 Plant | CO2 Plant | 1 | NY | Navy | Demolition | Building | Navy | 2006 | 1200 |  | m2 | 5 | 3 | 1 | 1 | 1 | 3800 | 0 | 1 | 10 |  | 0 |  | 4560000 | 89420 | 3 | - The CO2 plant is in very poor condition. - all structural members are rusted - Roofs are dilapidated | - Cerberus/Tenant to give additional instruction of the future usage of the building
42 | Contingencies (10%) | CO2 Plant | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 10 |  | 0 | 0 | 83600 | 1640 | 1 | - Contingencies | 10% contingencies
43 | Preliminaries (10%) | CO2 Plant | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92000 | 0 | 1 | 10 |  | 0 | 0 | 92000 | 1810 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
44 | Permitting and Engineering (5%) | CO2 Plant | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4600 | 0 | 1 | 10 |  | 0 | 0 | 4600 | 100 | 1 | - Soft Cost | - Permitting and Engineering
45 | Overall structural retrofitting | Piping Pre-treatment building Galva | 1 | NY | Navy | Structural Elements | Structural | Navy | 2011 | 2900 |  | m2 | 5 | 3 | 1 | 3 | 0.7 | 5000 | 0 | 1 | 0 |  | 1 | 166400 | 10150000 | 199020 | 1 | - The Galvanizing is in bad condition and needs to be retrofitted immediately. Steel frames are rusted and requires major removal of rust. | - full rehabilitation of structural elements including replacement of rusted steel elements
46 | Replacement of rusted GI wall sheet | Piping Pre-treatment building Galva | 1 | NY | Navy | Building Fabric | Architectural | Navy | 2011 | 3000 |  | m2 | 5 | 3 | 1 | 3 | 0.8 | 2500 | 0 | 1 | 0 |  | 1 | 248625 | 6000000 | 117650 | 1 | - Sections of the façade are rusted and needs to be replaced | -replacement of GI sheet façade
47 | Replacement of GI roofing including insulation | Piping Pre-treatment building Galva | 1 | NY | Navy | Roof | Roof | Navy | 2011 | 3200 |  | m2 | 5 | 3 | 1 | 3 | 0.8 | 2800 | 0 | 1 | 0 |  | 1 | 464000 | 7168000 | 140550 | 1 | - Sections of the façade are rusted and needs to be replaced | - replacement of GI sheet roof
48 | Replacement of all electrical wirings | Piping Pre-treatment building Galva | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 2900 |  | m2 | 5 | 3 | 1 | 3 | 1 | 4000 | 50 | 1 | 0 |  | 1 | 208000 | 11600000 | 227460 | 1 | - all electrical wirings need to be replaced due to the previous facility usage. | - Replacement of electrical wirings and cables
48 | Replacement of all electrical wirings | Piping Pre-treatment building Galva | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 2900 |  | m2 | 0 | 3 | 1 | 8 | 1 | 4000 | 50 | 0 | 25 |  | 1 | 145600 | 0 | 0 | 0 | - due to the change of usage, service life of the electrical wires will be further extended to its maximum life expectancy | - No CapEx will be included in Phase 2
49 | New Protective Coating | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 1 |  | lot | 5 | 3 | 1 | 4 | 1 | 2565300 | 0 | 1 | 0 |  | 1 | 50300 | 2565300 | 50300 | 1 | - most columns are rusted; however, can still be used and only needs to be rehabilitated by removing the rust and apply new protective coating | - Repainting of rusted structural steel to protect the steel from re-rusting
50 | Replacement of sliding door (7mx9m) | Piping Pre-treatment building Galva | 1 | NY | Navy | Building Fabric | Architectural | Navy | 2011 | 2 |  | unit | 5 | 3 | 1 | 5 | 1 | 540000 | 0 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Sliding door is already damaged - rollers are rusted and are stocked in one place | - total replacement of sliding doors
51 | Filling and concreting (200mm) of tanks | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 420 |  | m3 | 0 | 3 | 1 | 6 | 1 | 700 | 0 | 1 | 0 |  | 0 | 0 | 294000 | 5770 | 3 | - Philippine Navy will change the current usage of the building | - Filling and concreting of the galvanizing tanks to suit PN requirement
52 | Rehabiltation of control room for the gantry of the Crane/hoist (PN Navy admin bldg and Control room) | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 50 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 100000 | 1970 | 3 | - The current usage of the area is for the control room of the gantry. - Philippine navy plans to keep the room as a admin building | - Rehabilitation of the room to comply with admin building; - Repainting of Walls - Rubberized floorings - Replacement of damaged ceilings
53 | Warehouse Building - Damage Ceiling | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 140 |  | m2 | 5 | 3 | 1 | 5 | 1 | 720 | 15 | 1 | 0 |  | 0 | 0 | 100800 | 1980 | 1 | - Ceiling is damage due to earthquake | - Replacement of ceiling
54 | Miscellaneous Items | Piping Pre-treatment building Galva | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1953000 | 0 | 1 | 0 |  | 0 | 0 | 1953000 | 38300 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal
55 | Contingencies (10%) | Piping Pre-treatment building Galva | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4101200 | 0 | 1 | 0 |  | 0 | 0 | 4101200 | 80420 | 1 | - Contingencies | 10% contingencies
56 | Preliminaries (10%) | Piping Pre-treatment building Galva | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4511300 | 0 | 1 | 0 |  | 0 | 0 | 4511300 | 88460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
57 | Permitting and Engineering (5%) | Piping Pre-treatment building Galva | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2481200 | 0 | 1 | 0 |  | 0 | 0 | 2481200 | 48660 | 1 | - Soft Cost | - Permitting and Engineering
58 | Repair of Missing 12mm Dia Rod Brace including accessories | Painting Shop A -1 | 1 | NY | Navy | Structural Elements | Structural | Navy | 2006 | 60 |  | kg | 5 | 3 | 1 | 5 | 1 | 200 | 0 | 1 | 0 |  | 0 | 0 | 12000 | 240 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
59 | Upgrade to comply current structural code | Painting Shop A -1 | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 860 |  | kg | 3 | 1 | 0 | 1 | 1 | 4000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2
60 | Replacement of GI Roof | Painting Shop A -1 | 1 | NY | Navy | Roof | Roof | Navy | 2006 | 860 |  | m2 | 5 | 3 | 1 | 2 | 0.5 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 1075000 | 21080 | 1 | - Most roofs are already rusted | - replacement of GI sheet roof
61 | Replacement of all electrical wirings | Painting Shop A -1 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 860 |  | m2 | 0 | 3 | 1 | 8 | 1 | 2500 | 25 | 1 | 11 |  | 0 | 0 | 2150000 | 42160 | 1 | - All electrical system are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement at end of life of conduit, wirings, electrical equipments such as lighting fixtures & wiring devices
62 | Miscellaneous Items | Painting Shop A -1 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 108700 | 0 | 1 | 0 |  | 0 | 0 | 108700 | 2140 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - Missing 12mm Dia Rod Brace including accessories - Removal of paint cavities - Broken Door Jambs and knobs | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal - Installation of missing 12mm dia rod brace - Replacement of door Jambs and knobs - Repainting of rusted steel members
63 | Contingencies (10%) | Painting Shop A -1 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 119600 | 0 | 1 | 0 |  | 0 | 0 | 119600 | 2350 | 1 | - Contingencies | 10% contingencies
64 | Preliminaries (10%) | Painting Shop A -1 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 131600 | 0 | 1 | 0 |  | 0 | 0 | 131600 | 2590 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
65 | Permitting and Engineering (5%) | Painting Shop A -1 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 72400 | 0 | 1 | 0 |  | 0 | 0 | 72400 | 1420 | 1 | - Soft Cost | - Permitting and Engineering
66 | Replacement of mechanical louvers and insulation pads | Piping Shelter | 1 | NY | Navy | Mechanical System | Mechanical | Navy | 2012 | 1 |  | lot | 4 | 2 | 1 | 5 | 0.5 | 800000 | 0 | 1 | 2 |  | 0 | 0 | 400000 | 7850 | 1 | - louvers and insulation pads are damaged. | - replacement of louvers and insulation pads to retain its as-built condition - can still be used until 2 years
67 | Replacement of all electrical wirings | Piping Shelter | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 1000 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2500 | 25 | 1 | 17 |  | 0 |  | 2500000 | 49020 | 1 | - All electrical system are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement at end of life of conduit, wirings, electrical equipments such as lighting fixtures & wiring devices
68 | Upgrade to comply current structural code | Piping Shelter | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 0 | 1 | 1 | 4000 | 0 | 0.1 | 0 |  | 0 |  | 400000 | 7850 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
69 | Miscellaneous items | Piping Shelter | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 80000 | 0 | 1 | 0 |  | 0 |  | 80000 | 1570 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - Rusted Steel Frame members - Removal of paint cavities - Damaged Sliding Door Rubber Gasket | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal - Installation of missing 12mm dia rod brace - Repainting of rusted steel members - Replacement of damaged steel gasket
70 | Contingencies (10%) | Piping Shelter | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 88000 | 0 | 1 | 0 |  | 0 | 0 | 88000 | 1730 | 1 | - Contingencies | 10% contingencies
71 | Preliminaries (10%) | Piping Shelter | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 96800 | 0 | 1 | 0 |  | 0 | 0 | 96800 | 1900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
72 | Permitting and Engineering (5%) | Piping Shelter | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 53300 | 0 | 1 | 0 |  | 0 | 0 | 53300 | 1050 | 1 | - Soft Cost | - Permitting and Engineering |  | - Assumed tiles to be used are ceramic tiles and not stone or marble tiles
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 3 | 3 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 93000 | 1830 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition |  | - Assumed tiles to be used are ceramic tiles and not stone or marble tiles
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 | 0 | 93000 | 1830 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy |  | - Assumed tiles to be used are ceramic tiles and not stone or marble tiles
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 | 0 | 93000 | 1830 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 75000 | 1480 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 | 0 | 75000 | 1480 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
75 | Replacement of Ceiling Boards | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 11 |  | 0 | 0 | 186000 | 3650 | 1 | - Ceiling Boards are still in good condition | - Installation of new ceiling boards due to life expectancy
76 | Replacement of DX type units | Field Office 14 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2016 | 16 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 6 |  | 0 | 0 | 2208000 | 43300 | 1 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service
76 | Replacement of DX type units | Field Office 14 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2016 | 16 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 16 |  | 0 | 0 | 2208000 | 43300 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
77 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 14 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 310 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 310000 | 6080 | 2 | - All wires are messed up and are scattered around the places which is a tripping hazard. | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
78 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 14 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 310 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 620000 | 12160 | 2 | - All auxiliary wires are in fair condition but still re-usable - All IT components such as CCTV and ID scanner are in fair condition. -All wires are messed and are scattered around the places which is a tripping hazard. | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
79 | Repair of roofs and gutters | Field Office 14 | Lot | NY | Navy | Roof | Roof | Navy | 2016 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from broken downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
80 | Miscellaneous items | Field Office 14 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 81840 | 0 | 1 | 0 |  | 0 | 0 | 81840 | 1610 | 1 | - Allocation for the unforeseen repair/installation such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace
81 | Contingencies (10%) | Field Office 14 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110500 | 0 | 1 | 0 |  | 0 | 0 | 110500 | 2170 | 1 | - Contingencies | 10% contingencies
82 | Preliminaries (10%) | Field Office 14 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121600 | 0 | 1 | 0 |  | 0 | 0 | 121600 | 2390 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
83 | Permitting and Engineering (5%) | Field Office 14 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66900 | 0 | 1 | 0 |  | 0 | 0 | 66900 | 1320 | 1 | - Soft Cost | - Permitting and Engineering
84 | Generator Set | Main Generator Room | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 7.5 |  | MW | 3 | 1 | 1 | 8 | 1 | 13500000 | 30 | 1 | 15 |  | 0 | 0 | 101250000 | 1985300 | 1 | - Generator has at least 30 years of life expectancy. If properly maintained, this equipment can be prolonged | - Replacement of Generator due to end of life
85 | Overall Repair of the Facility | Main Generator Room | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 75000 | 0 | 1 | 0 |  | 0 | 0 | 75000 | 1480 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages
86 | Contingencies (10%) | Main Generator Room | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 7500 | 0 | 1 | 0 |  | 0 | 0 | 7500 | 150 | 1 | - Contingencies | 10% contingencies
87 | Preliminaries (10%) | Main Generator Room | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 8300 | 0 | 1 | 0 |  | 0 | 0 | 8300 | 170 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
88 | Permitting and Engineering (5%) | Main Generator Room | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4600 | 0 | 1 | 0 |  | 0 | 0 | 4600 | 100 | 1 | - Soft Cost | - Permitting and Engineering
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 5 | 2 | 1 | 3 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 60000 | 1180 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 60000 | 1180 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 60000 | 1180 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
91 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - Accommodation | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 70 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 70000 | 1380 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
92 | Miscellaneous Items | Barracks - Accommodation | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 17200 | 0 | 1 | 0 |  | 0 |  | 17200 | 340 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
93 | Contingencies (10%) | Barracks - Accommodation | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 18900 | 0 | 1 | 0 |  | 0 | 0 | 18900 | 380 | 1 | - Contingencies | 10% contingencies
94 | Preliminaries (10%) | Barracks - Accommodation | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 20800 | 0 | 1 | 0 |  | 0 | 0 | 20800 | 410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
95 | Permitting and Engineering (5%) | Barracks - Accommodation | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 11500 | 0 | 1 | 0 |  | 0 | 0 | 11500 | 230 | 1 | - Soft Cost | - Permitting and Engineering
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
97 | Supply and installation of linoleum flooring | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 195000 | 3830 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
97 | Supply and installation of linoleum flooring | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 195000 | 3830 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 5 | 2 | 1 | 5 | 1 | 45000 | 10 | 1 | 0 |  | 0 | 0 | 4815000 | 94420 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 10 |  | 0 | 0 | 4815000 | 94420 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 20 |  | 0 | 0 | 4815000 | 94420 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
99 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 200 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 400000 | 7850 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
100 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - C | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1300000 | 25500 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
101 | Miscellaneous Items | Barracks - C | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 617800 | 0 | 1 | 0 |  | 0 |  | 617800 | 12120 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
102 | Contingencies (10%) | Barracks - C | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 834100 | 0 | 1 | 0 |  | 0 | 0 | 834100 | 16360 | 1 | - Contingencies | 10% contingencies
103 | Preliminaries (10%) | Barracks - C | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 917500 | 0 | 1 | 0 |  | 0 | 0 | 917500 | 18000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
104 | Permitting and Engineering (5%) | Barracks - C | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 504600 | 0 | 1 | 0 |  | 0 | 0 | 504600 | 9900 | 1 | - Soft Cost | - Permitting and Engineering
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
106 | Supply and installation of linoleum flooring | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 780 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 117000 | 2300 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
106 | Supply and installation of linoleum flooring | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 780 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 117000 | 2300 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 0 | 10 |  | 1 | 489000 | 0 | 0 | 0 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC moved to immediate to retain its as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 3150000 | 61770 | 1 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
108 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 130 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 260000 | 5100 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
109 | Panel Boards | Barracks - B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 346290 | 25 | 0 | 11 |  | 1 | 6790 | 0 | 0 | 0 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
110 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 780 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 780000 | 15300 | 1 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
111 | Miscellaneous Items | Barracks - B | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 291200 | 0 | 1 | 0 |  | 0 |  | 291200 | 5710 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
112 | Contingencies (10%) | Barracks - B | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 393100 | 0 | 1 | 0 |  | 0 | 0 | 393100 | 7710 | 1 | - Contingencies | 10% contingencies
113 | Preliminaries (10%) | Barracks - B | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 432400 | 0 | 1 | 0 |  | 0 | 0 | 432400 | 8480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
114 | Permitting and Engineering (5%) | Barracks - B | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 237900 | 0 | 1 | 0 |  | 0 | 0 | 237900 | 4670 | 1 | - Soft Cost | - Permitting and Engineering
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
116 | Supply and installation of linoleum flooring | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 | 0 | 225000 | 4420 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
116 | Supply and installation of linoleum flooring | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 | 0 | 225000 | 4420 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 1 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 1 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 1 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
118 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 150 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 300000 | 5890 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
119 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - Admin | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
120 | Miscellaneous Items | Barracks - Admin | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 380800 | 0 | 1 | 0 |  |  | 0 | 380800 | 7470 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
121 | Contingencies (10%) | Barracks - Admin | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 514100 | 0 | 1 | 0 |  | 0 | 0 | 514100 | 10090 | 1 | - Contingencies | 10% contingencies
122 | Preliminaries (10%) | Barracks - Admin | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 565500 | 0 | 1 | 0 |  | 0 | 0 | 565500 | 11090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
123 | Permitting and Engineering (5%) | Barracks - Admin | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 311100 | 0 | 1 | 0 |  | 0 | 0 | 311100 | 6100 | 1 | - Soft Cost | - Permitting and Engineering
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
125 | Supply and installation of linoleum flooring | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1100 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 165000 | 3240 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
125 | Supply and installation of linoleum flooring | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 165000 | 3240 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
126 | Replacement of Wooden Flooring to 6mm steel plate | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 52250 |  | kg | 0 | 1 | 1 | 8 | 1 | 250 | 20 | 1 | 20 |  | 0 |  | 13062500 | 256130 | 1 | - Wooden floors are already decaying due to termites | - replacement of wooden floors to steel plate.
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 1 |  | 1830000 | 35890 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 |  | 1830000 | 35890 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 |  | 1830000 | 35890 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
128 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - G1 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1100 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1100000 | 21570 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
129 | Miscellaneous Items | Barracks - G1 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 397000 | 0 | 1 | 0 |  |  | 0 | 397000 | 7790 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of comfort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of comfort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
130 | Contingencies (10%) | Barracks - G1 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 436700 | 0 | 1 | 0 |  | 0 | 0 | 436700 | 8570 | 1 | - Contingencies | 10% contingencies
131 | Preliminaries (10%) | Barracks - G1 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 480400 | 0 | 1 | 0 |  | 0 | 0 | 480400 | 9420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
132 | Permitting and Engineering (5%) | Barracks - G1 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 264300 | 0 | 1 | 0 |  | 0 | 0 | 264300 | 5190 | 1 | - Soft Cost | - Permitting and Engineering
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
134 | Supply and installation of linoleum flooring | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 225000 | 4420 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
134 | Supply and installation of linoleum flooring | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 225000 | 4420 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
136 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - G2 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1500000 | 29420 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
137 | Miscellaneous Items | Barracks - G2 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 356800 | 0 | 1 | 0 |  |  | 0 | 356800 | 7000 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
138 | Contingencies (10%) | Barracks - G2 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 481700 | 0 | 1 | 0 |  | 0 | 0 | 481700 | 9450 | 1 | - Contingencies | 10% contingencies
139 | Preliminaries (10%) | Barracks - G2 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 529900 | 0 | 1 | 0 |  | 0 | 0 | 529900 | 10400 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
140 | Permitting and Engineering (5%) | Barracks - G2 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 291500 | 0 | 1 | 0 |  | 0 | 0 | 291500 | 5720 | 1 | - Soft Cost | - Permitting and Engineering
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
142 | Supply and installation of linoleum flooring | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 157500 | 3090 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
142 | Supply and installation of linoleum flooring | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 157500 | 3090 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 5 | 2 | 1 | 5 | 1 | 45000 | 10 | 1 | 0 |  | 0 | 0 | 3780000 | 74120 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 10 |  | 0 | 0 | 3780000 | 74120 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 20 |  | 0 | 0 | 3780000 | 74120 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
144 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - D | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1050000 | 20590 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
145 | Miscellaneous Items | Barracks - D | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 465000 | 0 | 1 | 0 |  |  |  | 465000 | 9120 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
146 | Contingencies (10%) | Barracks - D | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 627800 | 0 | 1 | 0 |  | 0 | 0 | 627800 | 12310 | 1 | - Contingencies | 10% contingencies
147 | Preliminaries (10%) | Barracks - D | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 690600 | 0 | 1 | 0 |  | 0 | 0 | 690600 | 13550 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
148 | Permitting and Engineering (5%) | Barracks - D | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 379800 | 0 | 1 | 0 |  | 0 | 0 | 379800 | 7450 | 1 | - Soft Cost | - Permitting and Engineering
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
150 | Supply and installation of linoleum flooring | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 195000 | 3830 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
150 | Supply and installation of linoleum flooring | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 195000 | 3830 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 3150000 | 61770 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
152 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 200 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 400000 | 7850 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
153 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - E | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
154 | Contingencies (10%) | Barracks - E | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 605800 | 0 | 1 | 0 |  | 0 | 0 | 605800 | 11880 | 1 | - Contingencies | 10% contingencies
155 | Preliminaries (10%) | Barracks - E | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 666400 | 0 | 1 | 0 |  | 0 | 0 | 666400 | 13070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
156 | Permitting and Engineering (5%) | Barracks - E | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 366500 | 0 | 1 | 0 |  | 0 | 0 | 366500 | 7190 | 1 | - Soft Cost | - Permitting and Engineering
157 | Overall Repair of the Facility | Convenience Store building | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 502 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 2 |  | 1 | 63100 | 2510000 | 49220 | 1 | - Cracks on Slab - Exhaust Fan Damage - Comfort Room stained and Filthy - House Cleaning - Damage Doors 2m x 2.1 m (1no) -Canopy Rusted - Korean brand socket - Repainting | Repair of this building will be dependend with the user. Assumed repaired within 2 years - Repairs of Slab - Replacement of Exhaust Fan - House cleaning - Replacement of Door 2mx2.1m (1no.) - Repainting of Canopy - Rehabilitation of comfor room - Replacement of Korean brand outlet to 3-prong universal socket - Repainting
158 | Contingencies (10%) | Convenience Store building | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 251000 | 0 | 1 | 2 |  | 0 | 0 | 251000 | 4930 | 1 | - Contingencies | 10% contingencies
159 | Preliminaries (10%) | Convenience Store building | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 276100 | 0 | 1 | 2 |  | 0 | 0 | 276100 | 5420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
160 | Permitting and Engineering (5%) | Convenience Store building | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 151900 | 0 | 1 | 2 |  | 0 | 0 | 151900 | 2980 | 1 | - Soft Cost | - Permitting and Engineering
161 | Overall Repair of the Facility | Canteen-Romanian | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 220 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 2 |  | 0 | 0 | 1100000 | 21570 | 1 | - Cracks on Slab - Exhaust Fan Damage - Comfort Room stained and Filthy - House Cleaning - Damage Doors 2m x 2.1 m (1no) -Canopy Rusted - Korean brand socket | - Repairs of Slab - Replacement of Exhaust Fan - House cleaning - Replacement of Door 2mx2.1m (1no.) - Repainting of Canopy - Rehabilitation of comfor room - Replacement of Korean brand outlet to 3-prong universal socket
162 | Contingencies (10%) | Canteen-Romanian | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110000 | 0 | 1 | 2 |  | 0 | 0 | 110000 | 2160 | 1 | - Contingencies | 10% contingencies
163 | Preliminaries (10%) | Canteen-Romanian | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121000 | 0 | 1 | 2 |  | 0 | 0 | 121000 | 2380 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
164 | Permitting and Engineering (5%) | Canteen-Romanian | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66600 | 0 | 1 | 2 |  | 0 | 0 | 66600 | 1310 | 1 | - Soft Cost | - Permitting and Engineering
165 | Overall Repair of the Facility | Air Compressed Room - 2,3 | 1 | NY | Austal | Miscellaneous | Miscellaneous | Austal | 2016 | 382 |  | m2 | 2 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.4 | 0 |  | 1 | 87700 | 764000 | 14990 | 1 | - Missing Cross Rod Brace - Damage Roller-up door | - Replacement of Cross Rod Brace - Replacement of Roller-up Door 5m x9m (1no)
166 | Panel Boards | Air Compressed Room - 2,3 | 1 | NY | Austal | Electrical System | Electrical | Austal | 2016 | 1 |  | lot | 2 | 1 | 1 | 5 | 1 | 2559690 | 25 | 1 | 21 |  | 1 | 50190 | 2559690 | 50190 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
167 | Upgrade to comply current structural code | Air Compressed Room - 2,3 | 1 | NY | Austal | Structural Upgrade | Structural | Austal | 2016 | 382 |  | lot | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - No CapEx will be included in Phase 2
168 | Contingencies (10%) | Air Compressed Room - 2,3 | lot | NY | Austal | Contingencies | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76400 | 0 | 1 | 0 |  | 0 | 0 | 76400 | 1500 | 1 | - Contingencies | 10% contingencies
169 | Preliminaries (10%) | Air Compressed Room - 2,3 | lot | NY | Austal | Preliminaries | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84100 | 0 | 1 | 0 |  | 0 | 0 | 84100 | 1650 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
170 | Permitting and Engineering (5%) | Air Compressed Room - 2,3 | lot | NY | Austal | Engineering and Management | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46300 | 0 | 1 | 0 |  | 0 | 0 | 46300 | 910 | 1 | - Soft Cost | - Permitting and Engineering
171 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
172 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 15 | 1 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
174 | Repainting of Walls 1st Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 315000 | 6180 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
174 | Repainting of Walls 1st Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
175 | Replacement of Ceiling Boards | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 11 |  | 0 | 0 | 240000 | 4710 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
176 | Replacement of DX type units | Field Office 15 | 2 | NY | Austal | HVAC | Mechanical | Austal | 2016 | 20 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 2760000 | 54120 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
176 | Replacement of DX type units | Field Office 15 | 2 | NY | Austal | HVAC | Mechanical | Austal | 2016 | 20 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 2760000 | 54120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
177 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 15 | Lot | NY | Austal | Electrical System | Electrical | Austal | 2016 | 400 |  | m2 | 4 | 3 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
177 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 15 | Lot | NY | Austal | Electrical System | Electrical | Austal | 2016 | 400 |  | m2 | 1 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
178 | Repair of roofs and gutters | Field Office 15 | Lot | NY | Austal | Roof | Roof | Austal | 2016 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
179 | Miscellaneous Items | Field Office 15 | 1 | NY | Austal | Miscellaneous | Miscellaneous | Austal | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 460000 | 0 | 1 | 0 |  |  |  | 460000 | 9020 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs
180 | Contingencies (10%) | Field Office 15 | lot | NY | Austal | Contingencies | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 506000 | 0 | 1 | 0 |  | 0 | 0 | 506000 | 9930 | 1 | - Contingencies | 10% contingencies
181 | Preliminaries (10%) | Field Office 15 | lot | NY | Austal | Preliminaries | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 556600 | 0 | 1 | 0 |  | 0 | 0 | 556600 | 10920 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
182 | Permitting and Engineering (5%) | Field Office 15 | lot | NY | Austal | Engineering and Management | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 300200 | 0 | 1 | 0 |  | 0 | 0 | 300200 | 5890 | 1 | - Soft Cost | - Permitting and Engineering
183 | Overall Repair of the Facility | Main Gate | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1342 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.3 | 2 |  | 0 | 0 | 2013000 | 39480 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
184 | Upgrade to comply current structural code | Main Gate | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 1342 |  | m2 | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 39470 | 1610400 | 31580 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
185 | Contingencies (10%) | Main Gate | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 362400 | 0 | 1 | 0 |  | 0 | 0 | 362400 | 7110 | 1 | - Contingencies | 10% contingencies
186 | Preliminaries (10%) | Main Gate | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 398600 | 0 | 1 | 0 |  | 0 | 0 | 398600 | 7820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
187 | Permitting and Engineering (5%) | Main Gate | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 219300 | 0 | 1 | 0 |  | 0 | 0 | 219300 | 4300 | 1 | - Soft Cost | - Permitting and Engineering
188 | Overall Repair of the Facility | Shelter 712 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.3 | 0 |  | 0 | 0 | 1650000 | 32360 | 1 | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element
189 | Replacement of polycarbornate Roof | Shelter 712 | 1 | NY | Navy | Roof | Roof | Navy | 2006 | 160 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 1 | 12700 | 320000 | 6280 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
190 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Shelter 712 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 0 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
191 | Contingencies (10%) | Shelter 712 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Contingencies | 10% contingencies
192 | Preliminaries (10%) | Shelter 712 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 181500 | 0 | 1 | 0 |  | 0 | 0 | 181500 | 3560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
193 | Permitting and Engineering (5%) | Shelter 712 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 99900 | 0 | 1 | 0 |  | 0 | 0 | 99900 | 1960 | 1 | - Soft Cost | - Permitting and Engineering
194 | Provision for the storm drainage | Assembly Shop (D) | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2016 | 800 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 4000000 | 78440 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
195 | Upgrade to comply current structural code | Assembly Shop (D) | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2016 | 11880 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 342700 | 2376000 | 46590 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
196 | Replacement of polycarbornate Roof | Assembly Shop (D) | 1 | NY | Navy | Roof | Roof | Navy | 2016 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 1 | 57120 | 6600000 | 129420 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
197 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Assembly Shop (D) | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 21 |  | 0 | 16030 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
198 | Miscellaneous Items | Assembly Shop (D) | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 318800 | 0 | 1 | 0 |  | 0 | 0 | 318800 | 6260 | 1 | - Repainting of rusted steel frame members | - Repainting of rusted steel frame members
199 | Contingencies (10%) | Assembly Shop (D) | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 669500 | 0 | 1 | 0 |  | 0 | 0 | 669500 | 13130 | 1 | - Contingencies | 10% contingencies
200 | Preliminaries (10%) | Assembly Shop (D) | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 736500 | 0 | 1 | 0 |  | 0 | 0 | 736500 | 14450 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
201 | Permitting and Engineering (5%) | Assembly Shop (D) | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 405100 | 0 | 1 | 0 |  | 0 | 0 | 405100 | 7950 | 1 | - Soft Cost | - Permitting and Engineering
202 | Provision for the storm drainage | Blasting & Painting Shop E | 1 | NY | Navy | Plumbing System | Plumbing | Navy | 2016 | 250 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1250000 | 24510 | 2 | - Damage Downspout - No proper drainage of downspout | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element
203 | Upgrade to comply current structural code | Blasting & Painting Shop E | 1 | NY | Navy | Structural Upgrade | All Disciplines | Navy | 2016 | 5913 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 170570 | 1182600 | 23190 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
204 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop E | 1 | NY | Navy | Roof | Roof | Navy | 2016 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 0 | 6 |  | 1 | 284280 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
205 | Miscellaneous Items | Blasting & Painting Shop E | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 243300 | 0 | 1 | 0 |  | 0 | 0 | 243300 | 4780 | 1 | - Repainting of rusted steel frame members | - Repainting of rusted steel frame members
206 | Contingencies (10%) | Blasting & Painting Shop E | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 267600 | 0 | 1 | 0 |  | 0 | 0 | 267600 | 5250 | 1 | - Contingencies | 10% contingencies
207 | Preliminaries (10%) | Blasting & Painting Shop E | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 294400 | 0 | 1 | 0 |  | 0 | 0 | 294400 | 5780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
208 | Permitting and Engineering (5%) | Blasting & Painting Shop E | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 161900 | 0 | 1 | 0 |  | 0 | 0 | 161900 | 3180 | 1 | - Soft Cost | - Permitting and Engineering
209 | Provision for the storm drainage | Field Office 2A | Lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
210 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 216000 | 4240 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
211 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 216000 | 4240 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 30500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
214 | Replacement of Ceiling Boards | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 432000 | 8480 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
214 | Replacement of Ceiling Boards | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 432000 | 8480 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2484000 | 48710 | 1 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
216 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 2A | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 720000 | 14120 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
217 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 2A | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1440000 | 28240 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
218 | Repair of roofs and gutters | Field Office 2A | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 8500 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
219 | Miscellaneous items | Field Office 2A | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1152600 | 0 | 1 | 0 |  | 0 | 0 | 1152600 | 22600 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
220 | Contingencies (10%) | Field Office 2A | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1267900 | 0 | 1 | 0 |  | 0 | 0 | 1267900 | 24870 | 1 | - Contingencies | 10% contingencies
221 | Preliminaries (10%) | Field Office 2A | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1394700 | 0 | 1 | 0 |  | 0 | 0 | 1394700 | 27350 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
222 | Permitting and Engineering (5%) | Field Office 2A | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 767100 | 0 | 1 | 0 |  | 0 | 0 | 767100 | 15050 | 1 | - Soft Cost | - Permitting and Engineering
223 | Provision for the storm drainage | Field Office 2 | Lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
224 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 640 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 192000 | 3770 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
225 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 640 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 192000 | 3770 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 510 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 27000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 510 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 127500 | 2500 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
228 | Replacement of Ceiling Boards | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 432000 | 8480 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
228 | Replacement of Ceiling Boards | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 432000 | 8480 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2484000 | 48710 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
230 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 2 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 720000 | 14120 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
231 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 2 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1440000 | 28240 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
232 | Repair of roofs and gutters | Field Office 2 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
233 | Miscellaneous items | Field Office 2 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1145600 | 0 | 1 | 0 |  | 0 | 0 | 1145600 | 22470 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
234 | Contingencies (10%) | Field Office 2 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1260200 | 0 | 1 | 0 |  | 0 | 0 | 1260200 | 24710 | 1 | - Contingencies | 10% contingencies
235 | Preliminaries (10%) | Field Office 2 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1386200 | 0 | 1 | 0 |  | 0 | 0 | 1386200 | 27190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
236 | Permitting and Engineering (5%) | Field Office 2 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 762400 | 0 | 1 | 0 |  | 0 | 0 | 762400 | 14950 | 1 | - Soft Cost | - Permitting and Engineering
237 | Upgrade to comply current structural code | No.5 Dock Shelter | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 4950 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 136300 | 4950000 | 97060 | 2 | ` | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
238 | Replacement of Angle Cross Brace | No.5 Dock Shelter | 1 | SY | Austal | Structural Elements | Structural | Austal | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 1856400 | 0 | 0 | 0 |  | 1 | 36400 | 0 | 0 | 0 | - During our latest site inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
239 | Overall Repair of the facility | No.5 Dock Shelter | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 4950 |  | m2 | 3 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 2475000 | 48530 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of roof with holes | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of roof with holes
240 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | No.5 Dock Shelter | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 49840 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
241 | Replacement of polycarbornate Roof and Wall | No.5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 320 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 640000 | 12550 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
242 | Contingencies (10%) | No.5 Dock Shelter | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 742500 | 0 | 1 | 0 |  | 0 | 0 | 742500 | 14560 | 1 | - Contingencies | 10% contingencies
243 | Preliminaries (10%) | No.5 Dock Shelter | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 816800 | 0 | 1 | 0 |  | 0 | 0 | 816800 | 16020 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
244 | Permitting and Engineering (5%) | No.5 Dock Shelter | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 449300 | 0 | 1 | 0 |  | 0 | 0 | 449300 | 8810 | 1 | - Soft Cost | - Permitting and Engineering
245 | Upgrade to comply current structural code | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 17220 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 147120 | 17220000 | 337650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
246 | Repair of GI Roof and Wall | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 750 |  | m2 | 5 | 3 | 1 | 5 | 1 | 2500 | 50 | 1 | 0 |  | 1 | 114500 | 1875000 | 36770 | 1 | - observed that section of roofs has some holes | - repair of roofs
247 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 13790 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
248 | Overall Repair of the facility | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 17220 |  | m2 | 3 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.05 | 0 |  | 1 | 87700 | 4305000 | 84420 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of rusted GI sheet wall | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of rusted GI sheet wall
249 | Replacement of polycarbornate Roof and Wall | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 320 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 640000 | 12550 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
250 | Contingencies (10%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2340000 | 0 | 1 | 0 |  | 0 | 0 | 2340000 | 45890 | 1 | - Contingencies | 10% contingencies
251 | Preliminaries (10%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2574000 | 0 | 1 | 0 |  | 0 | 0 | 2574000 | 50480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
252 | Permitting and Engineering (5%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1415700 | 0 | 1 | 0 |  | 0 | 0 | 1415700 | 27760 | 1 | - Soft Cost | - Permitting and Engineering
253 | Upgrade to comply current structural code | Hatch cover Shelter | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2006 | 16000 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 912700 | 19200000 | 376480 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
254 | Repair of Roof Frames | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 116400 |  | kg | 5 | 1 | 1 | 5 | 0.2 | 200 | 0 | 1 | 0 |  | 1 | 22600 | 4656000 | 91300 | 1 | - Replacement of angle cross brace included in the Overall repair of the facility | - Replacement of angle cross brace included in the Overall repair of the facility
255 | Gas port/ Electrical Panel Location Provision of Barricade | Hatch cover Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 2632500 | 25 | 0 | 2 |  | 1 | 744500 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
255 | Gas port/ Electrical Panel Location Provision of Barricade | Hatch cover Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 2632500 | 25 | 1 | 0 |  | 1 |  | 2632500 | 51620 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
256 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Hatch cover Shelter | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 49840 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
257 | Replacement of polycarbornate Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 1716 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 343200 | 6730 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
257 | Replacement of polycarbornate Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 1716 |  | m2 | 1 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 3432000 | 67300 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
258 | Repair of GI Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 25200 |  | m2 | 5 | 1 | 1 | 2 | 0.05 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 3150000 | 61770 | 1 | - observed that section of roofs has some holes | - repair of roofs
259 | Miscellaneous Items | Hatch cover Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1499100 | 0 | 1 | 0 |  | 0 | 0 | 1499100 | 29400 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal
260 | Contingencies (10%) | Hatch cover Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3148100 | 0 | 1 | 0 |  | 0 | 0 | 3148100 | 61730 | 1 | - Contingencies | 10% contingencies
261 | Preliminaries (10%) | Hatch cover Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3462900 | 0 | 1 | 0 |  | 0 | 0 | 3462900 | 67900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
262 | Permitting and Engineering (5%) | Hatch cover Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1904600 | 0 | 1 | 0 |  | 0 | 0 | 1904600 | 37350 | 1 | - Soft Cost | - Permitting and Engineering
263 | Upgrade to comply current structural code | Dhouse Shelter | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2006 | 15180 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 452890 | 15180000 | 297650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
264 | Replacement of Angle Cross Brace | Dhouse Shelter | 1 | NY | Tenant 3 | Structural Elements | Structural | Tenant 3 | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 0 | 0 | 0 | 0 |  | 1 | 19300 | 0 | 0 | 0 | - During our latest site inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
265 | Gas port/ Electrical Panel Location Provision of Barricade | Dhouse Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 3276000 | 25 | 0 | 2 |  | 1 | 638200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
265 | Gas port/ Electrical Panel Location Provision of Barricade | Dhouse Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 3276000 | 25 | 1 | 0 |  | 1 |  | 3276000 | 64240 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
266 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Dhouse Shelter | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 36540 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
267 | Replacement of polycarbornate Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 2160 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
267 | Replacement of polycarbornate Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 2160 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 4320000 | 84710 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
268 | Repair of GI Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 24400 |  | m2 | 5 | 1 | 1 | 2 | 0.05 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 3050000 | 59810 | 1 | - observed that section of roofs has some holes | - repair of roofs
269 | Miscellaneous Items | Dhouse Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2237000 | 0 | 1 | 0 |  | 0 | 0 | 2237000 | 43870 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal
270 | Contingencies (10%) | Dhouse Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2460700 | 0 | 1 | 0 |  | 0 | 0 | 2460700 | 48250 | 1 | - Contingencies | 10% contingencies
271 | Preliminaries (10%) | Dhouse Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2706800 | 0 | 1 | 0 |  | 0 | 0 | 2706800 | 53080 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
272 | Permitting and Engineering (5%) | Dhouse Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1488800 | 0 | 1 | 0 |  | 0 | 0 | 1488800 | 29200 | 1 | - Soft Cost | - Permitting and Engineering
273 | Upgrade to comply current structural code | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2016 | 10800 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 311540 | 2160000 | 42360 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
274 | Gas port/ Electrical Panel Location Provision of Barricade | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2016 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 1768000 | 25 | 0 | 2 |  | 1 | 254200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gas port and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
274 | Gas port/ Electrical Panel Location Provision of Barricade | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2016 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 1768000 | 25 | 1 | 0 |  | 1 |  | 1768000 | 34670 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gas port and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
275 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2016 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 14560 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
276 | Replacement of polycarbornate Roof and Wall | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2016 | 10800 |  | m2 | 3 | 1 | 1 | 5 | 0.05 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
276 | Replacement of polycarbornate Roof and Wall | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2016 | 10800 |  | m2 | 1 | 1 | 1 | 8 | 0.5 | 2000 | 25 | 1 | 16 |  | 0 | 0 | 10800000 | 211770 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
277 | Provision for the storm drainage | Sub-Assembly Shop (94 bay) | Lot | SY | Tenant 3 | Plumbing System | Plumbing | Tenant 3 | 2016 | 450 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 2250000 | 44120 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
278 | Miscellaneous Items | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1088700 | 0 | 1 | 0 |  | 0 | 0 | 1088700 | 21350 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - connecting of downspout to the nearest drainage - cleaning and hauling - rusted members for repainting - peeled off paints
279 | Contingencies (10%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 834700 | 0 | 1 | 0 |  | 0 | 0 | 834700 | 16370 | 1 | - Contingencies | 10% contingencies
280 | Preliminaries (10%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 918200 | 0 | 1 | 0 |  | 0 | 0 | 918200 | 18010 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
281 | Permitting and Engineering (5%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 505000 | 0 | 1 | 0 |  | 0 | 0 | 505000 | 9910 | 1 | - Soft Cost | - Permitting and Engineering
282 | Upgrade to comply current structural code | Outfitting Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 5600 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.3 | 0 |  | 0 | 0 | 6720000 | 131770 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
283 | Replacement of polycarbornate Roof and Wall | Outfitting Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5600 |  | m2 | 3 | 1 | 1 | 5 | 0.05 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 560000 | 10990 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
283 | Replacement of polycarbornate Roof and Wall | Outfitting Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5600 |  | m2 | 1 | 1 | 1 | 8 | 0.5 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 5600000 | 109810 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
284 | Miscellaneous Items | Outfitting Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1456000 | 0 | 1 | 0 |  | 0 | 0 | 1456000 | 28550 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - fastening of steel storage racks | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - fastening of steel storage racks
285 | Contingencies (10%) | Outfitting Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 873600 | 0 | 1 | 0 |  | 0 | 0 | 873600 | 17130 | 1 | - Contingencies | 10% contingencies
286 | Preliminaries (10%) | Outfitting Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 961000 | 0 | 1 | 0 |  | 0 | 0 | 961000 | 18850 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
287 | Permitting and Engineering (5%) | Outfitting Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 528600 | 0 | 1 | 0 |  | 0 | 0 | 528600 | 10370 | 1 | - Soft Cost | - Permitting and Engineering
288 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 178200 | 3500 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
289 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 178200 | 3500 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 25400 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
292 | Replacement of Ceiling Boards | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 356400 | 6990 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
292 | Replacement of Ceiling Boards | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 356400 | 6990 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4140000 | 81180 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4140000 | 81180 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4140000 | 81180 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
294 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 5A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 594000 | 11650 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
295 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 5A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1188000 | 23300 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
296 | Repair of roofs and gutters | Field Office 5A | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 594 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7100 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
297 | Miscellaneous items | Field Office 5A | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 687500 | 0 | 1 | 0 |  | 0 | 0 | 687500 | 13490 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
298 | Contingencies (10%) | Field Office 5A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 756300 | 0 | 1 | 0 |  | 0 | 0 | 756300 | 14830 | 1 | - Contingencies | 10% contingencies
299 | Preliminaries (10%) | Field Office 5A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 831900 | 0 | 1 | 0 |  | 0 | 0 | 831900 | 16320 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
300 | Permitting and Engineering (5%) | Field Office 5A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 457600 | 0 | 1 | 0 |  | 0 | 0 | 457600 | 8980 | 1 | - Soft Cost | - Permitting and Engineering
301 | Repair of Structural Steel frame members | Electric Steel Outfitting Shop | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 99000 |  | kg | 4 | 3 | 1 | 5 | 0.2 | 200 | 0 | 1 | 0 |  | 1 | 88300 | 3960000 | 77650 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
302 | Upgrade to comply current structural code | Electric Steel Outfitting Shop | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 3300 |  | m2 | 4 | 3 | 0 | 5 | 1 | 4000 | 0 | 0.7 | 0 |  | 1 | 252730 | 9240000 | 181180 | 2 | -The building was constructed in 2012 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
303 | Replacement of polycarbornate Roof and Wall | Electric Steel Outfitting Shop | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 400 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 17 |  | 0 | 0 | 800000 | 15690 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
304 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Electric Steel Outfitting Shop | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 17 |  | 1 | 2730 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
305 | Miscellaneous Items | Electric Steel Outfitting Shop | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2640000 | 0 | 1 | 0 |  | 0 | 0 | 2640000 | 51770 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
306 | Contingencies (10%) | Electric Steel Outfitting Shop | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1584000 | 0 | 1 | 0 |  | 0 | 0 | 1584000 | 31060 | 1 | - Contingencies | 10% contingencies
307 | Preliminaries (10%) | Electric Steel Outfitting Shop | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1742400 | 0 | 1 | 0 |  | 0 | 0 | 1742400 | 34170 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
308 | Permitting and Engineering (5%) | Electric Steel Outfitting Shop | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 958400 | 0 | 1 | 0 |  | 0 | 0 | 958400 | 18800 | 1 | - Soft Cost | - Permitting and Engineering
309 | Overall Repair of the facility | Electric Steel Outfitting Shop (Building at the back) | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1000 |  | m2 | 5 | 3 | 1 | 5 | 1 | 5000 | 0 | 1 | 0 |  | 1 | 230500 | 5000000 | 98040 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
310 | Replacement of GI wall sheet | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 360 |  | m2 | 4 | 3 | 1 | 5 | 1 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 900000 | 17650 | 1 | - Roofs are damaged | - replacement of GI sheet roof
311 | Replacement of polycarbornate Roof | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 750 | 25 | 1 | 0 |  | 0 | 0 | 75000 | 1480 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
311 | Replacement of polycarbornate Roof | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 750 | 25 | 1 | 25 |  | 0 | 0 | 75000 | 1480 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
312 | Miscellaneous Items | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1195000 | 0 | 1 | 0 |  | 0 | 0 | 1195000 | 23440 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
313 | Contingencies (10%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 717000 | 0 | 1 | 0 |  | 0 | 0 | 717000 | 14060 | 1 | - Contingencies | 10% contingencies
314 | Preliminaries (10%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 788700 | 0 | 1 | 0 |  | 0 | 0 | 788700 | 15470 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
315 | Permitting and Engineering (5%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 433800 | 0 | 1 | 0 |  | 0 | 0 | 433800 | 8510 | 1 | - Soft Cost | - Permitting and Engineering
316 | Repair of C-purlins for GI Sheet Wall | Cable Cutting | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 13600 |  | kg | 4 | 2 | 1 | 5 | 1 | 200 | 50 | 1 | 0 |  | 0 | 0 | 2720000 | 53340 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
317 | Replacement of polycarbornate Roof and Wall | Cable Cutting | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 2040 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1224000 | 24000 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
317 | Replacement of polycarbornate Roof and Wall | Cable Cutting | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 2040 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 17 |  | 0 | 0 | 4080000 | 80000 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
318 | Upgrade to comply current structural code | Cable Cutting | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 1250 |  | m2 | 4 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 0 | 1250000 | 24510 | 2 | -The building was constructed in 2012 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
319 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Cable Cutting | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 17 |  | 1 | 2730 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
320 | Miscellaneous Items | Cable Cutting | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1038800 | 0 | 1 | 0 |  | 0 | 0 | 1038800 | 20370 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
321 | Contingencies (10%) | Cable Cutting | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 623300 | 0 | 1 | 0 |  | 0 | 0 | 623300 | 12230 | 1 | - Contingencies | 10% contingencies
322 | Preliminaries (10%) | Cable Cutting | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 685700 | 0 | 1 | 0 |  | 0 | 0 | 685700 | 13450 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
323 | Permitting and Engineering (5%) | Cable Cutting | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 377100 | 0 | 1 | 0 |  | 0 | 0 | 377100 | 7400 | 1 | - Soft Cost | - Permitting and Engineering
324 | Overall Repair of the Facility | Gasoline Station | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 300 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
325 | Contingencies (10%) | Gasoline Station | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Contingencies | 10% contingencies
326 | Preliminaries (10%) | Gasoline Station | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
327 | Permitting and Engineering (5%) | Gasoline Station | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Soft Cost | - Permitting and Engineering
328 | Overall Repair of the Facility | Helicopter Hangar | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 900 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 2250000 | 44120 | 1 | - Damage Rain gutter - Vinyl tile dilapidated - Korean socket - Repainting | - Damage Rain gutter - Vinyl tile dilapidated - Korean socket - Repainting
329 | Contingencies (10%) | Helicopter Hangar | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 225000 | 0 | 1 | 0 |  | 0 | 0 | 225000 | 4420 | 1 | - Contingencies | 10% contingencies
330 | Preliminaries (10%) | Helicopter Hangar | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 247500 | 0 | 1 | 0 |  | 0 | 0 | 247500 | 4860 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
331 | Permitting and Engineering (5%) | Helicopter Hangar | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 136200 | 0 | 1 | 0 |  | 0 | 0 | 136200 | 2680 | 1 | - Soft Cost | - Permitting and Engineering
332 | Upgrade to comply current structural code | Main Office | Lot | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 14000 |  | m2 | 5 | 2 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 0 | 14000000 | 274510 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
333 | Removal and Replacement of Carpets | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 15000 |  | m2 | 3 | 2 | 1 | 5 | 0.7 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 10500000 | 205890 | 4 | - Carpets are worn-out, stained, filty and dirty | - Removal and Installation of carpets,
334 | Replacement of Ceiling Boards | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 15000 |  | m2 | 3 | 2 | 1 | 5 | 0.5 | 600 | 0 | 1 | 0 |  | 1 | 37300 | 4500000 | 88240 | 1 | - Some ceiling boards are either sagging, stained damaged | - Replacement of ceiling boards to as-built condition
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 98300 | 2250000 | 44120 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 2250000 | 44120 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 2250000 | 44120 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
336 | Electrical Works (Installation and replacement of defective wirings, replacements of outlets including embedments) | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 15000 |  | m2 | 5 | 3 | 1 | 4 | 1 | 750 | 0 | 1 | 0 |  | 0 | 0 | 11250000 | 220590 | 1 | - All wires are messed and are scattered around the places which is a safety concern of tripping - Outlets are in korean brand | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition - Replacement of outlets to Philippines standard
337 | Electrical & Auxillary Equipments | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 15000 |  | m2 | 3 | 1 | 1 | 8 | 1 | 1000 | 30 | 1 | 16 |  | 0 | 0 | 15000000 | 294120 | 1 | -End of Life | -Replacement of All Panelboards, CCTV Equipments, PA/BGM Equipments, FDAS Equipments due to 30 yrs life span
338 | Removal and installation of waterproofing | Main Office | Roof | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1500 | 25 | 1 | 0 |  | 1 | 53900 | 5250000 | 102950 | 1 | - Machine room including the presidents room has stained water leaks on the ceiling | - Reinstallation of waterproofing
338 | Removal and installation of waterproofing | Main Office | Roof | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 1500 | 25 | 1 | 11 |  | 0 | 0 | 5250000 | 102950 | 1 | - life expectancy of water proofing | - Reinstallation of waterproofing
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 10 | 1 | 5 |  | 1 | 1952000 | 8000000 | 156870 | 2 | - one chiller system has a serious gushing of water and needs to be replace immediately - Current alternative solution is feasible; however, efficiency | - replacement of HVAC system
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 3 |  | lot | 0 | 1 | 1 | 8 | 0.2 | 8000000 | 30 | 1 | 5 |  | 0 | 0 | 4800000 | 94120 | 2 | - '- HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be use as gushing already provided alternative repair solution; however, efficiency cannot be maximize due to its condition. | - replacement of refrigerant and compressor to comply with the phase-out of the R22
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 30 | 1 | 16 |  | 0 | 0 | 16000000 | 313730 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
340 | Lifts | Main Office | Lot | NY | Navy | Vertical Transportation | Mechanical | Navy | 2006 | 1 |  | lot | 4 | 1 | 1 | 2 | 0.3 | 1500000 | 25 | 1 | 0 |  | 1 | 11800 | 450000 | 8830 | 1 | - Elevators does not comply with the overweight capacity | - testing of elevator
340 | Lifts | Main Office | Lot | NY | Navy | Vertical Transportation | Mechanical | Navy | 2006 | 3 |  | no. | 1 | 1 | 1 | 8 | 1 | 1500000 | 25 | 1 | 11 |  | 1 | 0 | 4500000 | 88240 | 1 | - Elevators does not comply with the overweight capacity | - testing of elevator
341 | Provision for the storm drainage | Main Office | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2006 | 350 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 164800 | 1750000 | 34320 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
342 | Panel Boards | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 642600 | 25 | 1 | 11 |  | 0 | 12600 | 642600 | 12600 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
343 | Miscellaneous items | Main Office | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 3137500 | 0 | 1 | 0 |  | 1 | 89800 | 3137500 | 61520 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms - Cleaning of exterior facade - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms - Cleaning of exterior facade - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities
344 | Miscellaneous items 2 | Main Office | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1462500 | 0 | 1 | 3 |  | 1 | 11600 | 1462500 | 28680 | 1 | - Allocation for the unforeseen repair/installation such as - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities | - Allocation for the unforeseen repair/installation such as - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities
345 | Contingencies (10%) | Main Office | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6735000 | 0 | 1 | 0 |  | 0 | 0 | 6735000 | 132060 | 1 | - Contingencies | 10% contingencies
346 | Preliminaries (10%) | Main Office | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 7408500 | 0 | 1 | 0 |  | 0 | 0 | 7408500 | 145270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
347 | Permitting and Engineering (5%) | Main Office | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4074700 | 0 | 1 | 0 |  | 0 | 0 | 4074700 | 79900 | 1 | - Soft Cost | - Permitting and Engineering
348 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
349 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 97500 | 1920 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 97500 | 1920 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
352 | Replacement of Ceiling Boards | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 259200 | 5090 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
352 | Replacement of Ceiling Boards | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 259200 | 5090 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3036000 | 59530 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
354 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 5 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 432000 | 8480 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
355 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 5 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
356 | Repair of roofs and gutters | Field Office 5 | Lot | NY | Navy | Roof | Roof | Navy | 2006 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
357 | Miscellaneous items | Field Office 5 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 403632 | 0 | 1 | 0 |  | 0 | 0 | 403632 | 7920 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
358 | Contingencies (10%) | Field Office 5 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 545000 | 0 | 1 | 0 |  | 0 | 0 | 545000 | 10690 | 1 | - Contingencies | 10% contingencies
359 | Preliminaries (10%) | Field Office 5 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 599500 | 0 | 1 | 0 |  | 0 | 0 | 599500 | 11760 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
360 | Permitting and Engineering (5%) | Field Office 5 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 329700 | 0 | 1 | 0 |  | 0 | 0 | 329700 | 6470 | 1 | - Soft Cost | - Permitting and Engineering
361 | Overall Repair of the Facility | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 3950 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 9875000 | 193630 | 1 | - Broken Controls of motorized sliding doors - dilapidated Rubber gasket of motorized sliding door - Steel storage rack not fixed - Container offices for rehabilitation | - Repair of controls of motorized sliding doors - Replacement of rubber gasket of motorized doors - installation of bolts of the storage steel racks - rehabilitation of contatiner offices
362 | Contingencies (10%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 987500 | 0 | 1 | 0 |  | 0 | 0 | 987500 | 19370 | 1 | - Contingencies | 10% contingencies
363 | Preliminaries (10%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1086300 | 0 | 1 | 0 |  | 0 | 0 | 1086300 | 21300 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
364 | Permitting and Engineering (5%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 597500 | 0 | 1 | 0 |  | 0 | 0 | 597500 | 11720 | 1 | - Soft Cost | - Permitting and Engineering
365 | Overall Repair of the Facility | Nagyantok Warehouse | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 650 |  | m2 | 3 | 1 | 1 | 4 | 0.7 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 1137500 | 22310 | 1 | - Container offices for rehabilitation | - Rehabilitation of contatiner offices
366 | Contingencies (10%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 113800 | 0 | 1 | 0 |  | 0 | 0 | 113800 | 2240 | 1 | - Contingencies | 10% contingencies
367 | Preliminaries (10%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 125200 | 0 | 1 | 0 |  | 0 | 0 | 125200 | 2460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
368 | Permitting and Engineering (5%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 68900 | 0 | 1 | 0 |  | 0 | 0 | 68900 | 1360 | 1 | - Soft Cost | - Permitting and Engineering
369 | Overall Repair of the Facility | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 360 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1800000 | 35300 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
370 | Contingencies (10%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
371 | Preliminaries (10%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
372 | Permitting and Engineering (5%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
373 | Overall Repair of the Facility | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 300 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
374 | Contingencies (10%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Contingencies | 10% contingencies
375 | Preliminaries (10%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
376 | Permitting and Engineering (5%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Soft Cost | - Permitting and Engineering
377 | Overall Repair of the Facility | Nagyantok Stock office | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 60 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 300000 | 5890 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
378 | Contingencies (10%) | Nagyantok Stock office | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 30000 | 0 | 1 | 0 |  | 0 | 0 | 30000 | 590 | 1 | - Contingencies | 10% contingencies
379 | Preliminaries (10%) | Nagyantok Stock office | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 33000 | 0 | 1 | 0 |  | 0 | 0 | 33000 | 650 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
380 | Permitting and Engineering (5%) | Nagyantok Stock office | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 18200 | 0 | 1 | 0 |  | 0 | 0 | 18200 | 360 | 1 | - Soft Cost | - Permitting and Engineering
381 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
382 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 42400 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 187500 | 3680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 187500 | 3680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
385 | Replacement of Ceiling Boards | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 780000 | 15300 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
385 | Replacement of Ceiling Boards | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 780000 | 15300 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 4485000 | 87950 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
387 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 11B | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
388 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 11B | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2600000 | 50990 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
389 | Repair of roofs and gutters | Field Office 11B | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 11800 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
390 | Miscellaneous items | Field Office 11B | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1543200 | 0 | 1 | 0 |  | 0 | 0 | 1543200 | 30260 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - damaged ceilings - Stained/Rusted Aluminum Glass Door | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Repair of damage ceiling - Restoration stained/rusted aluminum glass door
391 | Contingencies (10%) | Field Office 11B | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2083400 | 0 | 1 | 0 |  | 0 | 0 | 2083400 | 40860 | 1 | - Contingencies | 10% contingencies
392 | Preliminaries (10%) | Field Office 11B | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2291700 | 0 | 1 | 0 |  | 0 | 0 | 2291700 | 44940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
393 | Permitting and Engineering (5%) | Field Office 11B | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1260500 | 0 | 1 | 0 |  | 0 | 0 | 1260500 | 24720 | 1 | - Soft Cost | - Permitting and Engineering
394 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 253500 | 4980 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
395 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 253500 | 4980 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 36100 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 108750 | 2140 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 108750 | 2140 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
398 | Replacement of Ceiling Boards | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 507000 | 9950 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
398 | Replacement of Ceiling Boards | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 507000 | 9950 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2967000 | 58180 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5934000 | 116360 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5934000 | 116360 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5934000 | 116360 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
400 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 11A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 845000 | 16570 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
401 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 11A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1690000 | 33140 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
402 | Repair of roofs and gutters | Field Office 11A | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 10000 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
403 | Miscellaneous items | Field Office 11A | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1013400 | 0 | 1 | 0 |  | 0 | 0 | 1013400 | 19880 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
404 | Contingencies (10%) | Field Office 11A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1368100 | 0 | 1 | 0 |  | 0 | 0 | 1368100 | 26830 | 1 | - Contingencies | 10% contingencies
405 | Preliminaries (10%) | Field Office 11A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1504900 | 0 | 1 | 0 |  | 0 | 0 | 1504900 | 29510 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
406 | Permitting and Engineering (5%) | Field Office 11A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 827700 | 0 | 1 | 0 |  | 0 | 0 | 827700 | 16230 | 1 | - Soft Cost | - Permitting and Engineering
407 | Panel Boards | Sub Station #30 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
408 | Transformers repair | Sub Station #30 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
409 | Overall Repair of the facility | Sub Station #30 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 890 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 890000 | 17460 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
410 | Contingencies (10%) | Sub Station #30 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 139000 | 0 | 1 | 0 |  | 0 | 0 | 139000 | 2730 | 1 | - Contingencies | 10% contingencies
411 | Preliminaries (10%) | Sub Station #30 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 152900 | 0 | 1 | 0 |  | 0 | 0 | 152900 | 3000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
412 | Permitting and Engineering (5%) | Sub Station #30 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84100 | 0 | 1 | 0 |  | 0 | 0 | 84100 | 1650 | 1 | - Soft Cost | - Permitting and Engineering
413 | Panel Boards | Sub Station #24 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
414 | Transformers repair | Sub Station #24 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
415 | Overall Repair of the facility | Sub Station #24 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 340 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 340000 | 6670 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
416 | Contingencies (10%) | Sub Station #24 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84000 | 0 | 1 | 0 |  | 0 | 0 | 84000 | 1650 | 1 | - Contingencies | 10% contingencies
417 | Preliminaries (10%) | Sub Station #24 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92400 | 0 | 1 | 0 |  | 0 | 0 | 92400 | 1820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
418 | Permitting and Engineering (5%) | Sub Station #24 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 50900 | 0 | 1 | 0 |  | 0 | 0 | 50900 | 1000 | 1 | - Soft Cost | - Permitting and Engineering
419 | Upgrade to comply current structural code | Panel Shop | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 54983 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1586040 | 54983000 | 1078100 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
420 | Replacement of polycarbornate Roof and Wall | Panel Shop | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 54983 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1099660 | 21570 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
420 | Replacement of polycarbornate Roof and Wall | Panel Shop | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 54983 |  | m2 | 1 | 1 | 1 | 8 | 0.25 | 2000 | 25 | 1 | 14 |  | 1 | 2643400 | 27491500 | 539050 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
421 | Panel Boards | Panel Shop | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 3777060 | 25 | 0 | 11 |  | 1 | 74060 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
422 | Miscellaneous Items | Panel Shop | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 5608300 | 0 | 1 | 0 |  | 0 | 0 | 5608300 | 109970 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
423 | Contingencies (10%) | Panel Shop | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6169100 | 0 | 1 | 0 |  | 0 | 0 | 6169100 | 120970 | 1 | - Contingencies | 10% contingencies
424 | Preliminaries (10%) | Panel Shop | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6786100 | 0 | 1 | 0 |  | 0 | 0 | 6786100 | 133070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
425 | Permitting and Engineering (5%) | Panel Shop | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3732400 | 0 | 1 | 0 |  | 0 | 0 | 3732400 | 73190 | 1 | - Soft Cost | - Permitting and Engineering
426 | Panel Boards | Sub Station #23 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
427 | Transformers repair | Sub Station #23 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
428 | Overall Repair of the facility | Sub Station #23 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 410 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 410000 | 8040 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
429 | Contingencies (10%) | Sub Station #23 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 91000 | 0 | 1 | 0 |  | 0 | 0 | 91000 | 1790 | 1 | - Contingencies | 10% contingencies
430 | Preliminaries (10%) | Sub Station #23 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 100100 | 0 | 1 | 0 |  | 0 | 0 | 100100 | 1970 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
431 | Permitting and Engineering (5%) | Sub Station #23 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 55100 | 0 | 1 | 0 |  | 0 | 0 | 55100 | 1090 | 1 | - Soft Cost | - Permitting and Engineering
432 | Panel Boards | Sub station #22-1 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
433 | Transformers repair | Sub station #22-1 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
434 | Overall Repair of the facility | Sub station #22-1 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 685 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 685000 | 13440 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
435 | Contingencies (10%) | Sub station #22-1 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 118500 | 0 | 1 | 0 |  | 0 | 0 | 118500 | 2330 | 1 | - Contingencies | 10% contingencies
436 | Preliminaries (10%) | Sub station #22-1 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 130400 | 0 | 1 | 0 |  | 0 | 0 | 130400 | 2560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
437 | Permitting and Engineering (5%) | Sub station #22-1 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 71700 | 0 | 1 | 0 |  | 0 | 0 | 71700 | 1410 | 1 | - Soft Cost | - Permitting and Engineering
438 | Upgrade to comply current structural code | Blasting & Painting Shop C | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 15001 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 432730 | 15001000 | 294140 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
439 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop C | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 15001 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 0 | 14 |  | 1 | 721160 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
440 | Panel Boards | Blasting & Painting Shop C | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 1 | 20230 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
441 | Fire Suppression System | Blasting & Painting Shop C | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
442 | Miscellaneous Items | Blasting & Painting Shop C | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1500100 | 0 | 1 | 0 |  | 0 | 0 | 1500100 | 29420 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of sliding door motor gasket
443 | Contingencies (10%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1650200 | 0 | 1 | 0 |  | 0 | 0 | 1650200 | 32360 | 1 | - Contingencies | 10% contingencies
444 | Preliminaries (10%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1815200 | 0 | 1 | 0 |  | 0 | 0 | 1815200 | 35600 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
445 | Permitting and Engineering (5%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 998400 | 0 | 1 | 0 |  | 0 | 0 | 998400 | 19580 | 1 | - Soft Cost | - Permitting and Engineering
446 | Upgrade to comply current structural code | Blasting & Painting Shop D | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 15008 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 432900 | 15008000 | 294280 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
447 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop D | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 15008 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 0 | 14 |  | 1 | 721160 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
448 | Panel Boards | Blasting & Painting Shop D | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 1 | 20230 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
449 | Gas port/ Electrical Panel Location Provision of Barricade | Blasting & Painting Shop D | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 18009018 | 25 | 0 | 2 |  | 1 | 353117.65 | 0 | 0 | 0 | - there are no gas ports and electrical panel inside the building | - No Capex will be allocated to Phase 2
450 | Fire Suppression System | Blasting & Painting Shop D | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
451 | Miscellaneous Items | Blasting & Painting Shop D | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1500800 | 0 | 1 | 0 |  | 0 | 0 | 1500800 | 29430 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of sliding door motor gasket
452 | Contingencies (10%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1650900 | 0 | 1 | 0 |  | 0 | 0 | 1650900 | 32380 | 1 | - Contingencies | 10% contingencies
453 | Preliminaries (10%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1816000 | 0 | 1 | 0 |  | 0 | 0 | 1816000 | 35610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
454 | Permitting and Engineering (5%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 998800 | 0 | 1 | 0 |  | 0 | 0 | 998800 | 19590 | 1 | - Soft Cost | - Permitting and Engineering
455 | Upgrade to comply current structural code | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 18983 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 147120 | 18983000 | 372220 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
456 | Replacement of polycarbornate Roof and Wall | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 18983 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 379660 | 7450 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
456 | Replacement of polycarbornate Roof and Wall | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 18983 |  | m2 | 3 | 1 | 1 | 8 | 0.1 | 2000 | 25 | 1 | 14 |  | 1 | 24520 | 3796600 | 74450 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
457 | Panel Boards | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1895670 | 25 | 0 | 11 |  | 1 | 37170 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
458 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3003000 | 25 | 0 | 2 |  | 1 | 649200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
458 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3003000 | 25 | 1 | 0 |  | 1 |  | 3003000 | 58890 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
459 | Miscellaneous Items | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1936300 | 0 | 1 | 0 |  | 1 | 21800 | 1936300 | 37970 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
460 | Contingencies (10%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2430200 | 0 | 1 | 0 |  | 0 | 0 | 2430200 | 47660 | 1 | - Contingencies | 10% contingencies
461 | Preliminaries (10%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2673300 | 0 | 1 | 0 |  | 0 | 0 | 2673300 | 52420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
462 | Permitting and Engineering (5%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1470300 | 0 | 1 | 0 |  | 0 | 0 | 1470300 | 28830 | 1 | - Soft Cost | - Permitting and Engineering
463 | Upgrade to comply current structural code | Hull Shop B | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 38920 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 342960 | 38920000 | 763140 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
464 | Replacement of polycarbornate Roof and Wall | Hull Shop B | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 38920 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 778400 | 15270 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
464 | Replacement of polycarbornate Roof and Wall | Hull Shop B | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 38920 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 14 |  | 1 | 160170 | 7784000 | 152630 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
465 | Panel Boards | Hull Shop B | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 123760 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
466 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop B | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3276000 | 25 | 0 | 2 |  | 1 | 744500 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
466 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop B | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3276000 | 25 | 1 | 0 |  | 1 |  | 3276000 | 64240 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
467 | Miscellaneous Items | Hull Shop B | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 3969900 | 0 | 1 | 0 |  | 0 | 0 | 3969900 | 77850 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
468 | Contingencies (10%) | Hull Shop B | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4694500 | 0 | 1 | 0 |  | 0 | 0 | 4694500 | 92050 | 1 | - Contingencies | 10% contingencies
469 | Preliminaries (10%) | Hull Shop B | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5163900 | 0 | 1 | 0 |  | 0 | 0 | 5163900 | 101260 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
470 | Permitting and Engineering (5%) | Hull Shop B | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2840200 | 0 | 1 | 0 |  | 0 | 0 | 2840200 | 55700 | 1 | - Soft Cost | - Permitting and Engineering
471 | Removal and Installation of vinyl tiles | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 714750 | 14020 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
472 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 285900 | 5610 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 27000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 129750 | 2550 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 1 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 129750 | 2550 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
475 | Replacement of Ceiling Boards | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 571800 | 11220 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
475 | Replacement of Ceiling Boards | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 571800 | 11220 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 3312000 | 64950 | 2 | - Some of the cassettes are already damaged and needs replacement | - remain to reuse the ACCU until the end of life service of the refrigerants
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3312000 | 64950 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 6624000 | 129890 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
478 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 8 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 48 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 48000 | 950 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
479 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 8 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1906000 | 37380 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
480 | Repair of roofs and gutters | Field Office 8 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
481 | Miscellaneous items | Field Office 8 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1305600 | 0 | 1 | 0 |  | 0 | 0 | 1305600 | 25600 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Repairs of slab
482 | Contingencies (10%) | Field Office 8 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1762500 | 0 | 1 | 0 |  | 0 | 0 | 1762500 | 34560 | 1 | - Contingencies | 10% contingencies
483 | Preliminaries (10%) | Field Office 8 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1938800 | 0 | 1 | 0 |  | 0 | 0 | 1938800 | 38020 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
484 | Permitting and Engineering (5%) | Field Office 8 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1066400 | 0 | 1 | 0 |  | 0 | 0 | 1066400 | 20910 | 1 | - Soft Cost | - Permitting and Engineering
485 | Upgrade to comply current structural code | Assembly shop (B) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 40562 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1170090 | 40562000 | 795340 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
486 | Replacement of polycarbornate Roof and Wall | Assembly shop (B) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 811240 | 15910 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
486 | Replacement of polycarbornate Roof and Wall | Assembly shop (B) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 195010 | 16224800 | 318140 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
487 | Panel Boards | Assembly shop (B) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 123760 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
488 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (B) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 0.7 | 14423500 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
488 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (B) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 0.7 | 14423500 | 25 | 1 | 0 |  | 1 |  | 10096450 | 197970 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
489 | Miscellaneous Items | Assembly shop (B) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2068700 | 0 | 1 | 0 |  | 0 | 0 | 2068700 | 40570 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
490 | Contingencies (10%) | Assembly shop (B) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5353900 | 0 | 1 | 0 |  | 0 | 0 | 5353900 | 104980 | 1 | - Contingencies | 10% contingencies
491 | Preliminaries (10%) | Assembly shop (B) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5889300 | 0 | 1 | 0 |  | 0 | 0 | 5889300 | 115480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
492 | Permitting and Engineering (5%) | Assembly shop (B) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3239100 | 0 | 1 | 0 |  | 0 | 0 | 3239100 | 63520 | 1 | - Soft Cost | - Permitting and Engineering
493 | Removal and Installation of vinyl tiles | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 607500 | 11920 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
494 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 243000 | 4770 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 34700 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 157500 | 3090 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 157500 | 3090 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
497 | Replacement of Ceiling Boards | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 486000 | 9530 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
497 | Replacement of Ceiling Boards | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 486000 | 9530 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2829000 | 55480 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 10 |  | 0 | 0 | 5658000 | 110950 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 20 |  | 0 | 0 | 5658000 | 110950 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
499 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 6a | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 810000 | 15890 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
500 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 6a | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1620000 | 31770 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
501 | Repair of roofs and gutters | Field Office 6a | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 22000 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
502 | Miscellaneous items | Field Office 6a | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 630300 | 0 | 1 | 0 |  | 0 | 0 | 630300 | 12360 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Comfort Room Rehabilitation | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Comfort Room Rehabilitation
503 | Contingencies (10%) | Field Office 6a | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 693400 | 0 | 1 | 0 |  | 0 | 0 | 693400 | 13600 | 1 | - Contingencies | 10% contingencies
504 | Preliminaries (10%) | Field Office 6a | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 762700 | 0 | 1 | 0 |  | 0 | 0 | 762700 | 14960 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
505 | Permitting and Engineering (5%) | Field Office 6a | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 419500 | 0 | 1 | 0 |  | 0 | 0 | 419500 | 8230 | 1 | - Soft Cost | - Permitting and Engineering
506 | Panel Boards | Sub station #11 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
507 | Transformers repair | Sub station #11 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
508 | Provision for the storm drainage | Sub station #11 | 1 | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 100 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 |  | 500000 | 9810 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
509 | Overall Repair of the facility | Sub station #11 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 800 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
510 | Contingencies (10%) | Sub station #11 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
511 | Preliminaries (10%) | Sub station #11 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
512 | Permitting and Engineering (5%) | Sub station #11 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
513 | Upgrade to comply current structural code | Welding Inspection Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 5000 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 138470 | 5000000 | 98040 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
514 | Replacement of polycarbornate Roof and Wall | Welding Inspection Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5000 |  | m2 | 3 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 2000000 | 39220 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
515 | Miscellaneous Items | Welding Inspection Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 750000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - repair of steel rung ladder - Installation of missing anchor bolts | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - repair of steel rung ladder - Installation of missing anchor bolts
516 | Contingencies (10%) | Welding Inspection Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 575000 | 0 | 1 | 0 |  | 0 | 0 | 575000 | 11280 | 1 | - Contingencies | 10% contingencies
517 | Preliminaries (10%) | Welding Inspection Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 632500 | 0 | 1 | 0 |  | 0 | 0 | 632500 | 12410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
518 | Permitting and Engineering (5%) | Welding Inspection Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 347900 | 0 | 1 | 0 |  | 0 | 0 | 347900 | 6830 | 1 | - Soft Cost | - Permitting and Engineering
519 | Panel Boards | Sub Station #37 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
520 | Transformers repair | Sub Station #37 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
521 | Overall Repair of the facility | Sub Station #37 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 250 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
522 | Contingencies (10%) | Sub Station #37 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 109800 | 0 | 1 | 0 |  | 0 | 0 | 109800 | 2160 | 1 | - Contingencies | 10% contingencies
523 | Preliminaries (10%) | Sub Station #37 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 120800 | 0 | 1 | 0 |  | 0 | 0 | 120800 | 2370 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
524 | Permitting and Engineering (5%) | Sub Station #37 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66500 | 0 | 1 | 0 |  | 0 | 0 | 66500 | 1310 | 1 | - Soft Cost | - Permitting and Engineering
525 | Upgrade to comply current structural code | Assembly shelter (6 nos) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 11130 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 685910 | 13356000 | 261890 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
526 | Replacement of polycarbornate Roof and Wall | Assembly shelter (6 nos) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 11130 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2226000 | 43650 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
526 | Replacement of polycarbornate Roof and Wall | Assembly shelter (6 nos) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 16224800 | 318140 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
527 | Miscellaneous Items | Assembly shelter (6 nos) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1558200 | 0 | 1 | 0 |  | 0 | 87700 | 1558200 | 30560 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Repair and replacement of buckled members | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Repair and replacement of buckled members
528 | Contingencies (10%) | Assembly shelter (6 nos) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1714100 | 0 | 1 | 0 |  | 0 | 0 | 1714100 | 33610 | 1 | - Contingencies | 10% contingencies
529 | Preliminaries (10%) | Assembly shelter (6 nos) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1885500 | 0 | 1 | 0 |  | 0 | 0 | 1885500 | 36980 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
530 | Permitting and Engineering (5%) | Assembly shelter (6 nos) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1037000 | 0 | 1 | 0 |  | 0 | 0 | 1037000 | 20340 | 1 | - Soft Cost | - Permitting and Engineering
531 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
532 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 93750 | 1840 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 93750 | 1840 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
535 | Replacement of Ceiling Boards | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 259200 | 5090 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
535 | Replacement of Ceiling Boards | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 259200 | 5090 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 1518000 | 29770 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
537 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 3 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 432000 | 8480 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
538 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 3 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
539 | Repair of roofs and gutters | Field Office 3 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
540 | Miscellaneous items | Field Office 3 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 524472 | 0 | 1 | 0 |  | 0 | 0 | 524472 | 10290 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
541 | Contingencies (10%) | Field Office 3 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 708100 | 0 | 1 | 0 |  | 0 | 0 | 708100 | 13890 | 1 | - Contingencies | 10% contingencies
542 | Preliminaries (10%) | Field Office 3 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 778900 | 0 | 1 | 0 |  | 0 | 0 | 778900 | 15280 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
543 | Permitting and Engineering (5%) | Field Office 3 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 421900 | 0 | 1 | 0 |  | 0 | 0 | 421900 | 8280 | 1 | - Soft Cost | - Permitting and Engineering
544 | Upgrade to comply current structural code | Pre-Outfitting Shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 8805 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 254000 | 8805000 | 172650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
545 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 8805 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 176100 | 3460 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
545 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 8805 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 3522000 | 69060 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
546 | Panel Boards | Pre-Outfitting Shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 19600 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
547 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 832000 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
547 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 832000 | 25 | 1 | 0 |  | 1 |  | 832000 | 16320 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
548 | Miscellaneous Items | Pre-Outfitting Shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 898200 | 0 | 1 | 0 |  | 0 | 0 | 898200 | 17620 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
549 | Contingencies (10%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1071200 | 0 | 1 | 0 |  | 0 | 0 | 1071200 | 21010 | 1 | - Contingencies | 10% contingencies
550 | Preliminaries (10%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1178300 | 0 | 1 | 0 |  | 0 | 0 | 1178300 | 23110 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
551 | Permitting and Engineering (5%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 648100 | 0 | 1 | 0 |  | 0 | 0 | 648100 | 12710 | 1 | - Soft Cost | - Permitting and Engineering
552 | Panel Boards | Sub station #21 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
553 | Transformers repair | Sub station #21 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
554 | Overall Repair of the facility | Sub station #21 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1300 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
555 | Contingencies (10%) | Sub station #21 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
556 | Preliminaries (10%) | Sub station #21 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
557 | Permitting and Engineering (5%) | Sub station #21 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
558 | Overall Repair of the facility | Steel Stock Yard | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 37275 |  | m2 | 0 | 1 | 1 | 5 | 0.02 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 3727500 | 73090 | 1 | - Soft Cost | - Permitting and Engineering
559 | Contingencies (10%) | Steel Stock Yard | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 372800 | 0 | 1 | 0 |  | 0 | 0 | 372800 | 7310 | 1 | - Contingencies | 10% contingencies
560 | Preliminaries (10%) | Steel Stock Yard | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 410100 | 0 | 1 | 0 |  | 0 | 0 | 410100 | 8050 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
561 | Permitting and Engineering (5%) | Steel Stock Yard | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 225600 | 0 | 1 | 0 |  | 0 | 0 | 225600 | 4430 | 1 | - Soft Cost | - Permitting and Engineering
562 | Panel Boards | Sub Station #16 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
563 | Transformers repair | Sub Station #16 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
564 | Provision for the storm drainage | Sub Station #16 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
565 | Overall Repair of the facility | Sub Station #16 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 360 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 360000 | 7060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
566 | Contingencies (10%) | Sub Station #16 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121000 | 0 | 1 | 0 |  | 0 | 0 | 121000 | 2380 | 1 | - Contingencies | 10% contingencies
567 | Preliminaries (10%) | Sub Station #16 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 133100 | 0 | 1 | 0 |  | 0 | 0 | 133100 | 2610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
568 | Permitting and Engineering (5%) | Sub Station #16 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 73300 | 0 | 1 | 0 |  | 0 | 0 | 73300 | 1440 | 1 | - Soft Cost | - Permitting and Engineering
569 | Structural Retrofitting and Rehabilitation (Upgrade to Code) | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 10564 |  | m2 | 5 | 3 | 0 | 4 | 1 | 4000 | 0 | 0 | 0 |  | 1 | 730800 | 0 | 0 | 2 | - substantial damaged found on the internal masonries of the building probably due to lack of shear restraining structures | - Full retrofit of the building is required such as - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
570 | Overall Repair of the facility (Building Envelope and interiors) | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Interior | Architectural | Austal | 2006 | 10564 |  | m2 | 5 | 3 | 1 | 4 | 0.5 | 27000 | 0 | 0 | 0 |  | 1 | 2885000 | 0 | 0 | 1 | - During the rehabilitatition, demolish and construct of damaged masonry walls, restoration of paints (interior and exterior),, rehabilitation of ceilings | - demolish and construct of CHB walls - Repainting of walls and ceiling - Restoration of Confort Rooms and Shower Rooms - Replacement of Ceiling boards
571 | Overall Repair of HVAC System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | HVAC | All Disciplines | Austal | 2006 | 529 |  | TR | 5 | 1 | 1 | 5 | 0.7 | 138000 | 30 | 0 | 0 |  | 1 | 35000 | 0 | 0 | 1 | - Most of the cassettes are already damaged and needs to e replaced. - During the rehabilitation, some of the HVAC ductings cannot be used and needs to be replaced | - Removal and replacement of the HVAC system
571 | Overall Repair of HVAC System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | HVAC | All Disciplines | Austal | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 138000 | 30 | 0 | 5 |  | 1 | 1077500 | 0 | 0 | 1 | - due to criticality, this item has been moved to immediate | - CapEx will be moved to immediate in Phase 2
572 | Overall Repair of Electrical System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Electrical System | Electrical | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 5 | 0.2 | 3300 | 0 | 0 | 0 |  | 1 | 109700 | 0 | 0 | 1 | -Due to rehabilitation, there will be wires that needs to be remove and replaced - Burnt-out lightings - damaged electrical auxilliaries (flourescent casings, outlets) | - Removal and Replacement of electrical and Auxilliary Wires
573 | Overall Repair of Plumbing | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 5 | 0.4 | 900 | 0 | 0 | 0 |  | 1 | 83800 | 0 | 0 | 1 | - During the rehabilitation, most pipes will need to be removed and replaced | - Removal and replacemnt of plumbing pipes
574 | Overall Repair of Waterproofing Membrane | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Roof | Roof | Austal | 2006 | 3521.3333 |  | m2 | 5 | 1 | 1 | 5 | 1 | 5500 | 25 | 0 | 0 |  | 1 | 410920 | 0 | 0 | 1 | - waterleaks are present inside the building due to the deterioration of the waterproof membrane | - Removal and Replacement of the waterproof membrane
575 | Demolition and Removal of PCC | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Demolition | Building | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 1 | 1 | 4000 | 0 | 1 | 10 |  | 0 | 0 | 42256000 | 828550 | 3
576 | Contingencies (10%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4225600 | 0 | 1 | 10 |  | 0 | 0 | 4225600 | 82860 | 1 | - Contingencies | 10% contingencies
577 | Preliminaries (10%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4648200 | 0 | 1 | 10 |  | 0 | 0 | 4648200 | 91150 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
578 | Permitting and Engineering (5%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2556500 | 0 | 1 | 10 |  | 0 | 0 | 2556500 | 50130 | 1 | - Soft Cost | - Permitting and Engineering
579 | Upgrade to comply current structural code | Blasting & Painting Shop B | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 13895 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 403300 | 13895000 | 272460 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
580 | Panel Boards | Blasting & Painting Shop B | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 0 | 0 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
581 | Fire Suppression System | Blasting & Painting Shop B | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
582 | Miscellaneous Items | Blasting & Painting Shop B | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1389500 | 0 | 1 | 0 |  | 0 | 0 | 1389500 | 27250 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - repair of motor for roller-up doors | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - repair of motor for roller-up doors
583 | Contingencies (10%) | Blasting & Painting Shop B | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1528500 | 0 | 1 | 0 |  | 0 | 0 | 1528500 | 29980 | 1 | - Contingencies | 10% contingencies
584 | Preliminaries (10%) | Blasting & Painting Shop B | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1681300 | 0 | 1 | 0 |  | 0 | 0 | 1681300 | 32970 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
585 | Permitting and Engineering (5%) | Blasting & Painting Shop B | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1849500 | 0 | 1 | 0 |  | 0 | 0 | 1849500 | 36270 | 1 | - Soft Cost | - Permitting and Engineering
586 | Overall Repair of the facility | Tool Shop | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 985 |  | m2 | 0 | 1 | 1 | 5 | 0.3 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1477500 | 28980 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
587 | Contingencies (10%) | Tool Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147800 | 0 | 1 | 0 |  | 0 | 0 | 147800 | 2900 | 1 | - Contingencies | 10% contingencies
588 | Preliminaries (10%) | Tool Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162600 | 0 | 1 | 0 |  | 0 | 0 | 162600 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
589 | Permitting and Engineering (5%) | Tool Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89400 | 0 | 1 | 0 |  | 0 | 0 | 89400 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
590 | Panel Boards | Sub Station #3 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
591 | Transformers repair | Sub Station #3 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
592 | Provision for the storm drainage | Sub Station #3 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
593 | Overall Repair of the facility | Sub Station #3 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 390 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
594 | Contingencies (10%) | Sub Station #3 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 124000 | 0 | 1 | 0 |  | 0 | 0 | 124000 | 2440 | 1 | - Contingencies | 10% contingencies
595 | Preliminaries (10%) | Sub Station #3 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 136400 | 0 | 1 | 0 |  | 0 | 0 | 136400 | 2680 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
596 | Permitting and Engineering (5%) | Sub Station #3 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 75100 | 0 | 1 | 0 |  | 0 | 0 | 75100 | 1480 | 1 | - Soft Cost | - Permitting and Engineering
597 | Panel Boards | Sub Station #10 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
598 | Transformers repair | Sub Station #10 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
599 | Provision for the storm drainage | Sub Station #10 | lot | SY | Dock 6 | Plumbing System | Plumbing | Dock 6 | 2009 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
600 | Overall Repair of the facility | Sub Station #10 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 207 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 207000 | 4060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
601 | Contingencies (10%) | Sub Station #10 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105700 | 0 | 1 | 0 |  | 0 | 0 | 105700 | 2080 | 1 | - Contingencies | 10% contingencies
602 | Preliminaries (10%) | Sub Station #10 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 116300 | 0 | 1 | 0 |  | 0 | 0 | 116300 | 2290 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
603 | Permitting and Engineering (5%) | Sub Station #10 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 64000 | 0 | 1 | 0 |  | 0 | 0 | 64000 | 1260 | 1 | - Soft Cost | - Permitting and Engineering
604 | Overall Repair of the facility | Fire Station | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 225 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1125000 | 22060 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
605 | Contingencies (10%) | Fire Station | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 141100 | 0 | 1 | 0 |  | 0 | 0 | 141100 | 2770 | 1 | - Contingencies | 10% contingencies
606 | Preliminaries (10%) | Fire Station | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 155300 | 0 | 1 | 0 |  | 0 | 0 | 155300 | 3050 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
607 | Permitting and Engineering (5%) | Fire Station | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170800 | 0 | 1 | 0 |  | 0 | 0 | 170800 | 3350 | 1 | - Soft Cost | - Permitting and Engineering
608 | Upgrade to comply current structural code | Maintenance Shop | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 1500 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 43120 | 1500000 | 29420 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
609 | Miscellaneous Items | Maintenance Shop | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
610 | Contingencies (10%) | Maintenance Shop | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Contingencies | 10% contingencies
611 | Preliminaries (10%) | Maintenance Shop | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 181500 | 0 | 1 | 0 |  | 0 | 0 | 181500 | 3560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
612 | Permitting and Engineering (5%) | Maintenance Shop | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 99900 | 0 | 1 | 0 |  | 0 | 0 | 99900 | 1960 | 1 | - Soft Cost | - Permitting and Engineering
613 | Upgrade to comply current structural code | Paint Can Stock Area | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 1550 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 44670 | 1550000 | 30400 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
614 | Fire Suppression System | Paint Can Stock Area | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 3462900 | 0 | 0 | 0 |  | 1 | 67900 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
615 | Miscellaneous Items | Paint Can Stock Area | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 155000 | 0 | 1 | 0 |  | 0 | 0 | 155000 | 3040 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
616 | Contingencies (10%) | Paint Can Stock Area | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170500 | 0 | 1 | 0 |  | 0 | 0 | 170500 | 3350 | 1 | - Contingencies | 10% contingencies
617 | Preliminaries (10%) | Paint Can Stock Area | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 187600 | 0 | 1 | 0 |  | 0 | 0 | 187600 | 3680 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
618 | Permitting and Engineering (5%) | Paint Can Stock Area | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 103200 | 0 | 1 | 0 |  | 0 | 0 | 103200 | 2030 | 1 | - Soft Cost | - Permitting and Engineering
619 | Overall Repair of the facility | Waste Matter/Scrap Iron Stock | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 2600 |  | m2 | 0 | 1 | 1 | 5 | 0.3 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 3900000 | 76480 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
620 | Contingencies (10%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 390000 | 0 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Contingencies | 10% contingencies
621 | Preliminaries (10%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 429000 | 0 | 1 | 0 |  | 0 | 0 | 429000 | 8420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
622 | Permitting and Engineering (5%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 236000 | 0 | 1 | 0 |  | 0 | 0 | 236000 | 4630 | 1 | - Soft Cost | - Permitting and Engineering
623 | Overall Repair of the facility | Barracks - K | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 2600 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.2 | 0 |  | 0 | 0 | 2600000 | 50990 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU
624 | Contingencies (10%) | Barracks - K | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 260000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Contingencies | 10% contingencies
625 | Preliminaries (10%) | Barracks - K | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 286000 | 0 | 1 | 0 |  | 0 | 0 | 286000 | 5610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
626 | Permitting and Engineering (5%) | Barracks - K | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 157300 | 0 | 1 | 0 |  | 0 | 0 | 157300 | 3090 | 1 | - Soft Cost | - Permitting and Engineering
627 | Overall Repair of the facility | Barracks - Romanian | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 210 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 525000 | 10300 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans
628 | Contingencies (10%) | Barracks - Romanian | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 52500 | 0 | 1 | 0 |  | 0 | 0 | 52500 | 1030 | 1 | - Contingencies | 10% contingencies
629 | Preliminaries (10%) | Barracks - Romanian | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 57800 | 0 | 1 | 0 |  | 0 | 0 | 57800 | 1140 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
630 | Permitting and Engineering (5%) | Barracks - Romanian | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 31800 | 0 | 1 | 0 |  | 0 | 0 | 31800 | 630 | 1 | - Soft Cost | - Permitting and Engineering
631 | Overall Repair of the facility | Barracks - F | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 700 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 1750000 | 34320 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU
632 | Contingencies (10%) | Barracks - F | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175000 | 0 | 1 | 0 |  | 0 | 0 | 175000 | 3440 | 1 | - Contingencies | 10% contingencies
633 | Preliminaries (10%) | Barracks - F | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192500 | 0 | 1 | 0 |  | 0 | 0 | 192500 | 3780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
634 | Permitting and Engineering (5%) | Barracks - F | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105900 | 0 | 1 | 0 |  | 0 | 0 | 105900 | 2080 | 1 | - Soft Cost | - Permitting and Engineering
635 | Overall Repair of the facility | Barracks - J | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 210 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 525000 | 10300 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans
636 | Contingencies (10%) | Barracks - J | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 52500 | 0 | 1 | 0 |  | 0 | 0 | 52500 | 1030 | 1 | - Contingencies | 10% contingencies
637 | Preliminaries (10%) | Barracks - J | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 57800 | 0 | 1 | 0 |  | 0 | 0 | 57800 | 1140 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
638 | Permitting and Engineering (5%) | Barracks - J | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 31800 | 0 | 1 | 0 |  | 0 | 0 | 31800 | 630 | 1 | - Soft Cost | - Permitting and Engineering
639 | Panel Boards | Sub Station #35 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
640 | Transformers repair | Sub Station #35 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
641 | Overall Repair of the facility | Sub Station #35 | 1 | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2009 | 260 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
642 | Contingencies (10%) | Sub Station #35 | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76000 | 0 | 1 | 0 |  | 0 | 0 | 76000 | 1500 | 1 | - Contingencies | 10% contingencies
643 | Preliminaries (10%) | Sub Station #35 | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
644 | Permitting and Engineering (5%) | Sub Station #35 | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46000 | 0 | 1 | 0 |  | 0 | 0 | 46000 | 910 | 1 | - Soft Cost | - Permitting and Engineering
645 | Panel Boards | Sub Station #34 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
646 | Transformers repair | Sub Station #34 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
647 | Overall Repair of the facility | Sub Station #34 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 260 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
648 | Contingencies (10%) | Sub Station #34 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76000 | 0 | 1 | 0 |  | 0 | 0 | 76000 | 1500 | 1 | - Contingencies | 10% contingencies
649 | Preliminaries (10%) | Sub Station #34 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
650 | Permitting and Engineering (5%) | Sub Station #34 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46000 | 0 | 1 | 0 |  | 0 | 0 | 46000 | 910 | 1 | - Soft Cost | - Permitting and Engineering
651 | Upgrade to comply current structural code | Assembly Shop (C) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 27025 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 779570 | 21620000 | 423930 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
652 | Replacement of polycarbornate Roof and Wall | Assembly Shop (C) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 27025 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 540500 | 10600 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
652 | Replacement of polycarbornate Roof and Wall | Assembly Shop (C) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 27025 |  | m2 | 3 | 1 | 1 | 5 | 0.5 | 2000 | 25 | 1 | 14 |  | 1 | 129930 | 27025000 | 529910 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
653 | Panel Boards | Assembly Shop (C) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1856400 | 25 | 0 | 11 |  | 1 | 36400 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
654 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly Shop (C) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 858000 | 25 | 0 | 2 |  | 1 | 635900 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
654 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly Shop (C) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 858000 | 25 | 1 | 0 |  | 1 |  | 858000 | 16830 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
655 | Miscellaneous Items | Assembly Shop (C) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2216100 | 0 | 1 | 0 |  | 0 | 0 | 2216100 | 43460 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
656 | Contingencies (10%) | Assembly Shop (C) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2523500 | 0 | 1 | 0 |  | 0 | 0 | 2523500 | 49490 | 1 | - Contingencies | 10% contingencies
657 | Preliminaries (10%) | Assembly Shop (C) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2775900 | 0 | 1 | 0 |  | 0 | 0 | 2775900 | 54430 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
658 | Permitting and Engineering (5%) | Assembly Shop (C) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1526700 | 0 | 1 | 0 |  | 0 | 0 | 1526700 | 29940 | 1 | - Soft Cost | - Permitting and Engineering
659 | Upgrade to comply current structural code | Blasting Shop A | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 5485.2 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 158230 | 4388160 | 86050 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
660 | Panel Boards | Blasting Shop A | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 378420 | 25 | 1 | 14 |  | 1 | 7420 | 378420 | 7420 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 5 | 3 | 1 | 5 | 1 | 140000 | 10 | 1 | 0 |  | 0 | 0 | 280000 | 5500 | 1 | - Floor mounted ACU's not working according to Hanjin operator | - Replacement of AC
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 10 |  | 0 | 0 | 280000 | 5500 | 1 | - life expectancy of HVAC | - Replacement of AC due to life expectancy
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 20 |  | 0 | 0 | 280000 | 5500 | 1 | - life expectancy of HVAC | - Replacement of AC due to life expectancy
662 | Miscellaneous Items | Blasting Shop A | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1400500 | 0 | 1 | 0 |  | 0 | 0 | 1400500 | 27470 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - replacement of worn rubber protective covers | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - replacement of worn rubber protective covers
663 | Contingencies (10%) | Blasting Shop A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 606900 | 0 | 1 | 0 |  | 0 | 0 | 606900 | 11900 | 1 | - Contingencies | 10% contingencies
664 | Preliminaries (10%) | Blasting Shop A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 667600 | 0 | 1 | 0 |  | 0 | 0 | 667600 | 13100 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
665 | Permitting and Engineering (5%) | Blasting Shop A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 367200 | 0 | 1 | 0 |  | 0 | 0 | 367200 | 7200 | 1 | - Soft Cost | - Permitting and Engineering
666 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 235500 | 4620 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
667 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 235500 | 4620 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 45200 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 357500 | 7010 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 357500 | 7010 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
670 | Replacement of Ceiling Boards | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 471000 | 9240 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
670 | Replacement of Ceiling Boards | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 471000 | 9240 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
672 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 12 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 785000 | 15400 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
673 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 12 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1570000 | 30790 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
674 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 99 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
675 | Repair of roofs and gutters | Field Office 12 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 12500 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
676 | Miscellaneous items | Field Office 12 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 973000 | 0 | 1 | 0 |  | 0 | 0 | 973000 | 19080 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room
677 | Contingencies (10%) | Field Office 12 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1070300 | 0 | 1 | 0 |  | 0 | 0 | 1070300 | 20990 | 1 | - Contingencies | 10% contingencies
678 | Preliminaries (10%) | Field Office 12 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1177400 | 0 | 1 | 0 |  | 0 | 0 | 1177400 | 23090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
679 | Permitting and Engineering (5%) | Field Office 12 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 647600 | 0 | 1 | 0 |  | 0 | 0 | 647600 | 12700 | 1 | - Soft Cost | - Permitting and Engineering
680 | Removal and Installation of vinyl tiles | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 431250 | 8460 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
681 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 172500 | 3390 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 24500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
684 | Replacement of Ceiling Boards | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 345000 | 6770 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
684 | Replacement of Ceiling Boards | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 345000 | 6770 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
686 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 7 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 575000 | 11280 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
687 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 7 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1150000 | 22550 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
688 | Repair of roofs and gutters | Field Office 7 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 575 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 6800 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
689 | Miscellaneous items | Field Office 7 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 972700 | 0 | 1 | 0 |  | 0 | 0 | 972700 | 19080 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Repair of damaged ceiling - Restoration of comfort rooms and Shower rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Repair of damaged ceiling - Restoration of comfort rooms and Shower rooms
690 | Contingencies (10%) | Field Office 7 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 745800 | 0 | 1 | 0 |  | 0 | 0 | 745800 | 14630 | 1 | - Contingencies | 10% contingencies
691 | Preliminaries (10%) | Field Office 7 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 820300 | 0 | 1 | 0 |  | 0 | 0 | 820300 | 16090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
692 | Permitting and Engineering (5%) | Field Office 7 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 451200 | 0 | 1 | 0 |  | 0 | 0 | 451200 | 8850 | 1 | - Soft Cost | - Permitting and Engineering
693 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 379500 | 7450 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
694 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 379500 | 7450 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 43500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
697 | Replacement of Ceiling Boards | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 759000 | 14890 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
697 | Replacement of Ceiling Boards | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 759000 | 14890 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
699 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 9 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1265000 | 24810 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
700 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 9 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2530000 | 49610 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
701 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 99 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
702 | Repair of roofs and gutters | Field Office 9 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 12100 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
703 | Miscellaneous items | Field Office 9 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1533300 | 0 | 1 | 0 |  | 0 | 0 | 1533300 | 30070 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room
704 | Contingencies (10%) | Field Office 9 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1686700 | 0 | 1 | 0 |  | 0 | 0 | 1686700 | 33080 | 1 | - Contingencies | 10% contingencies
705 | Preliminaries (10%) | Field Office 9 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1855300 | 0 | 1 | 0 |  | 0 | 0 | 1855300 | 36380 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
706 | Permitting and Engineering (5%) | Field Office 9 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1020500 | 0 | 1 | 0 |  | 0 | 0 | 1020500 | 20010 | 1 | - Soft Cost | - Permitting and Engineering
707 | Overall Repair of the facility | Filtration Plant | 1 | NY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 350 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 1 | 2 |  | 1 | 8900 | 1750000 | 34320 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door
708 | Contingencies (10%) | Filtration Plant | lot | NY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175000 | 0 | 1 | 2 |  | 0 | 0 | 175000 | 3440 | 1 | - Contingencies | 10% contingencies
709 | Preliminaries (10%) | Filtration Plant | lot | NY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192500 | 0 | 1 | 2 |  | 0 | 0 | 192500 | 3780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
710 | Permitting and Engineering (5%) | Filtration Plant | lot | NY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105900 | 0 | 1 | 2 |  | 0 | 0 | 105900 | 2080 | 1 | - Soft Cost | - Permitting and Engineering
711 | Upgrade to comply current structural code | Assembly shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 27390 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 537350 | 27390000 | 537060 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
712 | Replacement of polycarbornate Roof and Wall | Assembly shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 27390 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1643400 | 32230 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
712 | Replacement of polycarbornate Roof and Wall | Assembly shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 27390 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 12 |  | 1 | 89600 | 16434000 | 322240 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
713 | Panel Boards | Assembly shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 3134460 | 25 | 0 | 12 |  | 1 | 61460 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
714 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 0 | 2 |  | 0 | 0 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
714 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 1 | 0 |  | 0 | 0 | 3718000 | 72910 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
715 | Miscellaneous Items | Assembly shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2903400 | 0 | 1 | 0 |  | 0 | 0 | 2903400 | 56930 | 1 | Miscellaneous item includes: - connecting downspout to nearest drainage - repainting - fire extinguisher - cleaning and hauling | Miscellaneous item includes: - connecting downspout to nearest drainage - repainting - fire extinguisher - cleaning and hauling
716 | Contingencies (10%) | Assembly shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3565500 | 0 | 1 | 0 |  | 0 | 0 | 3565500 | 69920 | 1 | - Contingencies | 10% contingencies
717 | Preliminaries (10%) | Assembly shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3922100 | 0 | 1 | 0 |  | 0 | 0 | 3922100 | 76910 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
718 | Permitting and Engineering (5%) | Assembly shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2157200 | 0 | 1 | 0 |  | 0 | 0 | 2157200 | 42300 | 1 | - Soft Cost | - Permitting and Engineering
719 | Upgrade to comply current structural code | Hull Shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 37736 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1291740 | 37736000 | 739930 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
720 | Replacement of polycarbornate Roof and Wall | Hull Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 37736 |  | m2 | 3 | 1 | 1 | 5 | 0.035 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2641520 | 51800 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
720 | Replacement of polycarbornate Roof and Wall | Hull Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 37736 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 11 |  | 1 | 215290 | 22641600 | 443960 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
721 | Panel Boards | Hull Shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 5369280 | 25 | 0 | 11 |  | 1 | 105280 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
722 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 0 | 2 |  | 1 | 780400 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
722 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 1 | 0 |  | 1 |  | 3718000 | 72910 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
723 | Miscellaneous Items | Hull Shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 4037800 | 0 | 1 | 0 |  | 0 | 0 | 4037800 | 79180 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
724 | Contingencies (10%) | Hull Shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4813400 | 0 | 1 | 0 |  | 0 | 0 | 4813400 | 94390 | 1 | - Contingencies | 10% contingencies
725 | Preliminaries (10%) | Hull Shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5294700 | 0 | 1 | 0 |  | 0 | 0 | 5294700 | 103820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
726 | Permitting and Engineering (5%) | Hull Shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2912100 | 0 | 1 | 0 |  | 0 | 0 | 2912100 | 57100 | 1 | - Soft Cost | - Permitting and Engineering
727 | Upgrade to comply current structural code | Powerplant and Control Station | 1 | NY | JV | Structural Upgrade | Structural | Shared | 2006 | 1100 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.5 | 0 |  | 1 | 88840 | 2200000 | 43140 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 3 | 1 | 4 | 0.85 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 2337500 | 45840 | 1 | - replacement of roof due to damage | - Replacement of roof
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 4 | 1 | 2500 | 0 | 0 | 3 |  | 0 | 58500 | 0 | 0 | 1 | - due to criticality, repair of slab moved to immediate | - CapEx will be moved to immediate in Phase 2
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 4 | 1 | 2500 | 0 | 0 | 5 |  | 0 | 58500 | 0 | 0 | 1 | - due to criticality, repair of slab moved to immediate | - CapEx will be moved to immediate in Phase 2
729 | Overall Repair of Waterproofing Membrane | Powerplant and Control Station | 1 | NY | JV | Roof | Roof | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2500 | 25 | 1 | 0 |  | 1 | 65500 | 2750000 | 53930 | 1 | - waterleaks are present inside the building due to the deterioration of the waterproof membrane | - Removal and Replacement of the waterproof membrane
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 275000 | 5400 | 1 | - Wall paints are stained - Cracked on walls | - Repainting the wall to its as-built condition - Patching and Sealing of crack walls
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 275000 | 5400 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 275000 | 5400 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
731 | Panel Boards | Powerplant and Control Station | 1 | NY | JV | Electrical System | Electrical | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 82110 | 25 | 1 | 11 |  | 1 | 1610 | 82110 | 1610 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
732 | Miscellaneous Items | Powerplant and Control Station | lot | NY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 756300 | 0 | 1 | 0 |  | 0 | 0 | 756300 | 14830 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
733 | Contingencies (10%) | Powerplant and Control Station | lot | NY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 831900 | 0 | 1 | 0 |  | 0 | 0 | 831900 | 16320 | 1 | - Contingencies | 10% contingencies
734 | Preliminaries (10%) | Powerplant and Control Station | lot | NY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 915100 | 0 | 1 | 0 |  | 0 | 0 | 915100 | 17950 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
735 | Permitting and Engineering (5%) | Powerplant and Control Station | lot | NY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 503300 | 0 | 1 | 0 |  | 0 | 0 | 503300 | 9870 | 1 | - Soft Cost | - Permitting and Engineering
736 | Upgrade to comply current structural code | Pre Treatment Shop A | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 4662 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 92015 | 4662000 | 91420 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
737 | Replacement of polycarbornate Roof and Wall | Pre Treatment Shop A | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 4662 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 932400 | 18290 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
738 | Panel Boards | Pre Treatment Shop A | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 4305 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
739 | Gas port/ Electrical Panel Location Provision of Barricade | Pre Treatment Shop A | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3498600 | 25 | 0 | 2 |  | 1 | 68600 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
740 | Miscellaneous Items | Pre Treatment Shop A | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 466200 | 0 | 1 | 0 |  | 0 | 0 | 466200 | 9150 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
741 | Contingencies (10%) | Pre Treatment Shop A | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 512900 | 0 | 1 | 0 |  | 0 | 0 | 512900 | 10060 | 1 | - Contingencies | 10% contingencies
742 | Preliminaries (10%) | Pre Treatment Shop A | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 564200 | 0 | 1 | 0 |  | 0 | 0 | 564200 | 11070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
743 | Permitting and Engineering (5%) | Pre Treatment Shop A | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 310300 | 0 | 1 | 0 |  | 0 | 0 | 310300 | 6090 | 1 | - Soft Cost | - Permitting and Engineering
744 | Upgrade to comply current structural code | Pre Treatment Shop B | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 3362 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 92015 | 3362000 | 65930 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
745 | Replacement of polycarbornate Roof and Wall | Pre Treatment Shop B | 1 | SY | Austal | Roof | Roof | Dock 6 | 2006 | 3362 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 672400 | 13190 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
746 | Panel Boards | Pre Treatment Shop B | 1 | SY | Austal | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 4305 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
747 | Gas port/ Electrical Panel Location Provision of Barricade | Pre Treatment Shop B | 1 | SY | Austal | Fire Protection System | Fire Protection | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3498600 | 25 | 0 | 2 |  | 1 | 68600 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
748 | Miscellaneous Items | Pre Treatment Shop B | lot | SY | Austal | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 336200 | 0 | 1 | 0 |  | 0 | 0 | 336200 | 6600 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
749 | Contingencies (10%) | Pre Treatment Shop B | lot | SY | Austal | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 369900 | 0 | 1 | 0 |  | 0 | 0 | 369900 | 7260 | 1 | - Contingencies | 10% contingencies
750 | Preliminaries (10%) | Pre Treatment Shop B | lot | SY | Austal | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 406900 | 0 | 1 | 0 |  | 0 | 0 | 406900 | 7980 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
751 | Permitting and Engineering (5%) | Pre Treatment Shop B | lot | SY | Austal | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 223800 | 0 | 1 | 0 |  | 0 | 0 | 223800 | 4390 | 1 | - Soft Cost | - Permitting and Engineering
752 | Upgrade to comply current structural code | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 5734 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 164770 | 4587200 | 89950 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
753 | Repair of GI Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 2140 |  | m2 | 2 | 1 | 1 | 2 | 0.1 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 535000 | 10500 | 1 | - observed that section of roofs has some holes | - repair of roofs
754 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 5734 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 344040 | 6750 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
754 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 5734 |  | m2 | 0 | 1 | 1 | 8 | 0.3 | 2000 | 25 | 1 | 14 |  | 1 | 24520 | 3440400 | 67460 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
755 | Panel Boards | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 14 |  | 1 | 7700 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
756 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 988000 | 25 | 0 | 2 |  | 1 | 134400 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
756 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 988000 | 25 | 1 | 0 |  | 1 |  | 988000 | 19380 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
757 | Miscellaneous Items | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 546700 | 0 | 1 | 0 |  | 0 | 0 | 546700 | 10720 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
758 | Contingencies (10%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 700100 | 0 | 1 | 0 |  | 0 | 0 | 700100 | 13730 | 1 | - Contingencies | 10% contingencies
759 | Preliminaries (10%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 770200 | 0 | 1 | 0 |  | 0 | 0 | 770200 | 15110 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
760 | Permitting and Engineering (5%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 423600 | 0 | 1 | 0 |  | 0 | 0 | 423600 | 8310 | 1 | - Soft Cost | - Permitting and Engineering
761 | Overall Repair of the facility | Sewage Treatment Plant | 1 | SY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 1120 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 2800000 | 54910 | 2 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfort tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door - Crack on slab | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door - Repairs on crack slab
762 | Upgrade to comply DAO 2016 | Sewage Treatment Plant | lot | SY | JV | Plumbing System | Civil | Shared | 2006 | 1 |  | lot | 0 | 3 | 0 | 4 | 1 | 10000000 | 0 | 1 | 0 |  | 0 |  | 10000000 | 196080 | 2 | - Upgrade to comply DAO 2016 | - Rehabilitation of the STP to comply DAO 2016
763 | Contingencies (10%) | Sewage Treatment Plant | lot | SY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 280000 | 0 | 1 | 0 |  | 0 | 0 | 280000 | 5500 | 2 | - Contingencies | 10% contingencies
764 | Preliminaries (10%) | Sewage Treatment Plant | lot | SY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1308000 | 0 | 1 | 0 |  | 0 | 0 | 1308000 | 25650 | 2 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
765 | Permitting and Engineering (5%) | Sewage Treatment Plant | lot | SY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 719400 | 0 | 1 | 0 |  | 0 | 0 | 719400 | 14110 | 2 | - Soft Cost | - Permitting and Engineering
766 | Upgrade to comply current structural code | Sub Assembly Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 15560 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 378400 | 15560000 | 305100 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
767 | Replacement of polycarbornate Roof and Wall | Sub Assembly Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 15560 |  | m2 | 3 | 1 | 1 | 5 | 0.02 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 622400 | 12210 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
767 | Replacement of polycarbornate Roof and Wall | Sub Assembly Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 15560 |  | m2 | 0 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 63070 | 6224000 | 122040 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
768 | Panel Boards | Sub Assembly Shop | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 17710 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
769 | Gas port/ Electrical Panel Location Provision of Barricade | Sub Assembly Shop | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
769 | Gas port/ Electrical Panel Location Provision of Barricade | Sub Assembly Shop | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 1 | 0 |  | 1 |  | 3770000 | 73930 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
770 | Miscellaneous Items | Sub Assembly Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1618300 | 0 | 1 | 0 |  | 0 | 0 | 1618300 | 31740 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
771 | Contingencies (10%) | Sub Assembly Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2157100 | 0 | 1 | 0 |  | 0 | 0 | 2157100 | 42300 | 1 | - Contingencies | 10% contingencies
772 | Preliminaries (10%) | Sub Assembly Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2372800 | 0 | 1 | 0 |  | 0 | 0 | 2372800 | 46530 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
773 | Permitting and Engineering (5%) | Sub Assembly Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1305100 | 0 | 1 | 0 |  | 0 | 0 | 1305100 | 25600 | 1 | - Soft Cost | - Permitting and Engineering
774 | Panel Boards | Sub Station #13 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
775 | Transformers repair | Sub Station #13 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
776 | Overall Repair of the facility | Sub Station #13 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 371 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1113000 | 21830 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
777 | Contingencies (10%) | Sub Station #13 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 161300 | 0 | 1 | 0 |  | 0 | 0 | 161300 | 3170 | 1 | - Contingencies | 10% contingencies
778 | Preliminaries (10%) | Sub Station #13 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 177500 | 0 | 1 | 0 |  | 0 | 0 | 177500 | 3490 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
779 | Permitting and Engineering (5%) | Sub Station #13 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 97600 | 0 | 1 | 0 |  | 0 | 0 | 97600 | 1920 | 1 | - Soft Cost | - Permitting and Engineering
780 | Panel Boards | Sub Station #14 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
781 | Transformers repair | Sub Station #14 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
782 | Overall Repair of the facility | Sub Station #14 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 612 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1836000 | 36000 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
783 | Contingencies (10%) | Sub Station #14 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 233600 | 0 | 1 | 0 |  | 0 | 0 | 233600 | 4590 | 1 | - Contingencies | 10% contingencies
784 | Preliminaries (10%) | Sub Station #14 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 257000 | 0 | 1 | 0 |  | 0 | 0 | 257000 | 5040 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
785 | Permitting and Engineering (5%) | Sub Station #14 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 141400 | 0 | 1 | 0 |  | 0 | 0 | 141400 | 2780 | 1 | - Soft Cost | - Permitting and Engineering
786 | Panel Boards | Sub Station #15 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
787 | Transformers repair | Sub Station #15 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
788 | Overall Repair of the facility | Sub Station #15 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 332 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 996000 | 19530 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
789 | Contingencies (10%) | Sub Station #15 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 149600 | 0 | 1 | 0 |  | 0 | 0 | 149600 | 2940 | 1 | - Contingencies | 10% contingencies
790 | Preliminaries (10%) | Sub Station #15 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 164600 | 0 | 1 | 0 |  | 0 | 0 | 164600 | 3230 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
791 | Permitting and Engineering (5%) | Sub Station #15 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90600 | 0 | 1 | 0 |  | 0 | 0 | 90600 | 1780 | 1 | - Soft Cost | - Permitting and Engineering
792 | Panel Boards | Sub Station #36 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
793 | Transformers repair | Sub Station #36 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
794 | Overall Repair of the facility | Sub Station #36 | 1 | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 400 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1200000 | 23530 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
795 | Contingencies (10%) | Sub Station #36 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170000 | 0 | 1 | 0 |  | 0 | 0 | 170000 | 3340 | 1 | - Contingencies | 10% contingencies
796 | Preliminaries (10%) | Sub Station #36 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 187000 | 0 | 1 | 0 |  | 0 | 0 | 187000 | 3670 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
797 | Permitting and Engineering (5%) | Sub Station #36 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 102900 | 0 | 1 | 0 |  | 0 | 0 | 102900 | 2020 | 1 | - Soft Cost | - Permitting and Engineering
798 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 403800 | 7920 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
799 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 403800 | 7920 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 42000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
802 | Replacement of Ceiling Boards | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 807600 | 15840 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
802 | Replacement of Ceiling Boards | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 807600 | 15840 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 9384000 | 184000 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 9384000 | 184000 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 9384000 | 184000 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
804 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 1 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1346000 | 26400 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
805 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 1 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2692000 | 52790 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
806 | Repair of roofs and gutters | Field Office 1 | Lot | SY | Austal | Roof | Roof | Austal | 2008 | 1346 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 11700 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
807 | Miscellaneous items | Field Office 1 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1602800 | 0 | 1 | 0 |  | 0 | 0 | 1602800 | 31430 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
808 | Contingencies (10%) | Field Office 1 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1763000 | 0 | 1 | 0 |  | 0 | 0 | 1763000 | 34570 | 1 | - Contingencies | 10% contingencies
809 | Preliminaries (10%) | Field Office 1 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1939300 | 0 | 1 | 0 |  | 0 | 0 | 1939300 | 38030 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
810 | Permitting and Engineering (5%) | Field Office 1 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1066700 | 0 | 1 | 0 |  | 0 | 0 | 1066700 | 20920 | 1 | - Soft Cost | - Permitting and Engineering
811 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 323700 | 6350 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
812 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 323700 | 6350 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 32100 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 518750 | 10180 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 518750 | 10180 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
815 | Replacement of Ceiling Boards | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 647400 | 12700 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
815 | Replacement of Ceiling Boards | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 647400 | 12700 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 7452000 | 146120 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 7452000 | 146120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 7452000 | 146120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
817 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 10 | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1079000 | 21160 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
818 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 10 | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2158000 | 42320 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
819 | Repair of roofs and gutters | Field Office 10 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2008 | 1079 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 8900 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
820 | Miscellaneous items | Field Office 10 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1302200 | 0 | 1 | 0 |  | 0 | 0 | 1302200 | 25540 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
821 | Contingencies (10%) | Field Office 10 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1432400 | 0 | 1 | 0 |  | 0 | 0 | 1432400 | 28090 | 1 | - Contingencies | 10% contingencies
822 | Preliminaries (10%) | Field Office 10 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1575600 | 0 | 1 | 0 |  | 0 | 0 | 1575600 | 30900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
823 | Permitting and Engineering (5%) | Field Office 10 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 866600 | 0 | 1 | 0 |  | 0 | 0 | 866600 | 17000 | 1 | - Soft Cost | - Permitting and Engineering
824 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 234000 | 4590 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
825 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 234000 | 4590 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 9600 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 391500 | 7680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 391500 | 7680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
828 | Replacement of Ceiling Boards | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 468000 | 9180 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
828 | Replacement of Ceiling Boards | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 468000 | 9180 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5382000 | 105530 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5382000 | 105530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5382000 | 105530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
830 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 6 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 780000 | 15300 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
831 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 6 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1560000 | 30590 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
832 | Repair of roofs and gutters | Field Office 6 | Lot | SY | Austal | Roof | Roof | Austal | 2008 | 780 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 6100 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
833 | Miscellaneous items | Field Office 6 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 944100 | 0 | 1 | 0 |  | 0 | 0 | 944100 | 18520 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
834 | Contingencies (10%) | Field Office 6 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1038600 | 0 | 1 | 0 |  | 0 | 0 | 1038600 | 20370 | 1 | - Contingencies | 10% contingencies
835 | Preliminaries (10%) | Field Office 6 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1142400 | 0 | 1 | 0 |  | 0 | 0 | 1142400 | 22400 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
836 | Permitting and Engineering (5%) | Field Office 6 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 628400 | 0 | 1 | 0 |  | 0 | 0 | 628400 | 12330 | 1 | - Soft Cost | - Permitting and Engineering
837 | Upgrade to comply current structural code | Painting Shop A Ext. | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 10500 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 386990 | 10500000 | 205890 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
838 | Replacement of polycarbornate Roof and Wall | Painting Shop A Ext. | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10500 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 0 | 14 |  | 1 | 644960 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No CaPex will be added in the Phase 2
839 | Panel Boards | Painting Shop A Ext. | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 738990 | 25 | 0 | 14 |  | 1 | 14490 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
840 | Gas port/ Electrical Panel Location Provision of Barricade | Painting Shop A Ext. | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 0 | 2 |  | 1 | 253100 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
841 | Miscellaneous Items | Painting Shop A Ext. | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1050000 | 0 | 1 | 0 |  | 0 | 0 | 1050000 | 20590 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
842 | Contingencies (10%) | Painting Shop A Ext. | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1155000 | 0 | 1 | 0 |  | 0 | 0 | 1155000 | 22650 | 1 | - Contingencies | 10% contingencies
843 | Preliminaries (10%) | Painting Shop A Ext. | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1270500 | 0 | 1 | 0 |  | 0 | 0 | 1270500 | 24920 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
844 | Permitting and Engineering (5%) | Painting Shop A Ext. | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 698800 | 0 | 1 | 0 |  | 0 | 0 | 698800 | 13710 | 1 | - Soft Cost | - Permitting and Engineering
845 | Panel Boards | Sub Station #9 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
846 | Transformers repair | Sub Station #9 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
847 | Overall Repair of the facility | Sub Station #9 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 360 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
848 | Contingencies (10%) | Sub Station #9 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 158000 | 0 | 1 | 0 |  | 0 | 0 | 158000 | 3100 | 1 | - Contingencies | 10% contingencies
849 | Preliminaries (10%) | Sub Station #9 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 173800 | 0 | 1 | 0 |  | 0 | 0 | 173800 | 3410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
850 | Permitting and Engineering (5%) | Sub Station #9 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 95600 | 0 | 1 | 0 |  | 0 | 0 | 95600 | 1880 | 1 | - Soft Cost | - Permitting and Engineering
851 | Panel Boards | Sub station #12 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
852 | Transformers repair | Sub station #12 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
853 | Overall Repair of the facility | Sub station #12 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 735 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2205000 | 43240 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
854 | Contingencies (10%) | Sub station #12 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 270500 | 0 | 1 | 0 |  | 0 | 0 | 270500 | 5310 | 1 | - Contingencies | 10% contingencies
855 | Preliminaries (10%) | Sub station #12 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 297600 | 0 | 1 | 0 |  | 0 | 0 | 297600 | 5840 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
856 | Permitting and Engineering (5%) | Sub station #12 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 163700 | 0 | 1 | 0 |  | 0 | 0 | 163700 | 3210 | 1 | - Soft Cost | - Permitting and Engineering
857 | Panel Boards | Sub station #20 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
858 | Transformers repair | Sub station #20 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
859 | Overall Repair of the facility | Sub station #20 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 325 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 975000 | 19120 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
860 | Contingencies (10%) | Sub station #20 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147500 | 0 | 1 | 0 |  | 0 | 0 | 147500 | 2900 | 1 | - Contingencies | 10% contingencies
861 | Preliminaries (10%) | Sub station #20 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162300 | 0 | 1 | 0 |  | 0 | 0 | 162300 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
862 | Permitting and Engineering (5%) | Sub station #20 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89300 | 0 | 1 | 0 |  | 0 | 0 | 89300 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
863 | Panel Boards | Sub station #22 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
864 | Transformers repair | Sub station #22 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
865 | Overall Repair of the facility | Sub station #22 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 760 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2280000 | 44710 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
866 | Contingencies (10%) | Sub station #22 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 278000 | 0 | 1 | 0 |  | 0 | 0 | 278000 | 5460 | 1 | - Contingencies | 10% contingencies
867 | Preliminaries (10%) | Sub station #22 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 305800 | 0 | 1 | 0 |  | 0 | 0 | 305800 | 6000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
868 | Permitting and Engineering (5%) | Sub station #22 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 168200 | 0 | 1 | 0 |  | 0 | 0 | 168200 | 3300 | 1 | - Soft Cost | - Permitting and Engineering
869 | Panel Boards | Sub station #25 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
870 | Transformers repair | Sub station #25 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
871 | Overall Repair of the facility | Sub station #25 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 325 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 975000 | 19120 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
872 | Contingencies (10%) | Sub station #25 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147500 | 0 | 1 | 0 |  | 0 | 0 | 147500 | 2900 | 1 | - Contingencies | 10% contingencies
873 | Preliminaries (10%) | Sub station #25 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162300 | 0 | 1 | 0 |  | 0 | 0 | 162300 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
874 | Permitting and Engineering (5%) | Sub station #25 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89300 | 0 | 1 | 0 |  | 0 | 0 | 89300 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
875 | Panel Boards | Sub station #26 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
876 | Transformers repair | Sub station #26 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
877 | Overall Repair of the facility | Sub station #26 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 760 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2280000 | 44710 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
878 | Contingencies (10%) | Sub station #26 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 278000 | 0 | 1 | 0 |  | 0 | 0 | 278000 | 5460 | 1 | - Contingencies | 10% contingencies
879 | Preliminaries (10%) | Sub station #26 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 305800 | 0 | 1 | 0 |  | 0 | 0 | 305800 | 6000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
880 | Permitting and Engineering (5%) | Sub station #26 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 168200 | 0 | 1 | 0 |  | 0 | 0 | 168200 | 3300 | 1 | - Soft Cost | - Permitting and Engineering
881 | Panel Boards | Sub station #17 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
882 | Transformers repair | Sub station #17 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
883 | Overall Repair of the facility | Sub station #17 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 460 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1380000 | 27060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
884 | Contingencies (10%) | Sub station #17 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 188000 | 0 | 1 | 0 |  | 0 | 0 | 188000 | 3690 | 1 | - Contingencies | 10% contingencies
885 | Preliminaries (10%) | Sub station #17 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 206800 | 0 | 1 | 0 |  | 0 | 0 | 206800 | 4060 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
886 | Permitting and Engineering (5%) | Sub station #17 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 113800 | 0 | 1 | 0 |  | 0 | 0 | 113800 | 2240 | 1 | - Soft Cost | - Permitting and Engineering
887 | Panel Boards | Sub Station #31 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
888 | Transformers repair | Sub Station #31 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
889 | Overall Repair of the facility | Sub Station #31 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 320 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 960000 | 18830 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
890 | Contingencies (10%) | Sub Station #31 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 146000 | 0 | 1 | 0 |  | 0 | 0 | 146000 | 2870 | 1 | - Contingencies | 10% contingencies
891 | Preliminaries (10%) | Sub Station #31 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 160600 | 0 | 1 | 0 |  | 0 | 0 | 160600 | 3150 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
892 | Permitting and Engineering (5%) | Sub Station #31 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 88400 | 0 | 1 | 0 |  | 0 | 0 | 88400 | 1740 | 1 | - Soft Cost | - Permitting and Engineering
893 | Panel Boards | Sub Station #32 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
894 | Transformers repair | Sub Station #32 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
895 | Overall Repair of the facility | Sub Station #32 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 800 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2400000 | 47060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
896 | Contingencies (10%) | Sub Station #32 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 290000 | 0 | 1 | 0 |  | 0 | 0 | 290000 | 5690 | 1 | - Contingencies | 10% contingencies
897 | Preliminaries (10%) | Sub Station #32 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 319000 | 0 | 1 | 0 |  | 0 | 0 | 319000 | 6260 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
898 | Permitting and Engineering (5%) | Sub Station #32 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175500 | 0 | 1 | 0 |  | 0 | 0 | 175500 | 3450 | 1 | - Soft Cost | - Permitting and Engineering
899 | Panel Boards | Sub Station #38 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
900 | Transformers repair | Sub Station #38 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
901 | Overall Repair of the facility | Sub Station #38 | 1 | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 270 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 810000 | 15890 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
902 | Contingencies (10%) | Sub Station #38 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 131000 | 0 | 1 | 0 |  | 0 | 0 | 131000 | 2570 | 1 | - Contingencies | 10% contingencies
903 | Preliminaries (10%) | Sub Station #38 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 144100 | 0 | 1 | 0 |  | 0 | 0 | 144100 | 2830 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
904 | Permitting and Engineering (5%) | Sub Station #38 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 79300 | 0 | 1 | 0 |  | 0 | 0 | 79300 | 1560 | 1 | - Soft Cost | - Permitting and Engineering
905 | Overall Repair of the Facility | Air Compressed Room - 1 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 1342 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.3 | 2 |  | 0 | 0 | 2013000 | 39480 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
906 | Upgrade to comply current structural code | Air Compressed Room - 1 | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2006 | 1342 |  | m2 | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 33320 | 1610400 | 31580 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
907 | Contingencies (10%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 362400 | 0 | 1 | 0 |  | 0 | 0 | 362400 | 7110 | 1 | - Contingencies | 10% contingencies
908 | Preliminaries (10%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 398600 | 0 | 1 | 0 |  | 0 | 0 | 398600 | 7820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
909 | Permitting and Engineering (5%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 219300 | 0 | 1 | 0 |  | 0 | 0 | 219300 | 4300 | 1 | - Soft Cost | - Permitting and Engineering
910 | Overall Repair of the Facility | Samandra - Maintenance Shop/Office | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 1542 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 7710000 | 151180 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
911 | Contingencies (10%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 771000 | 0 | 1 | 0 |  | 0 | 0 | 771000 | 15120 | 1 | - Contingencies | 10% contingencies
912 | Preliminaries (10%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 848100 | 0 | 1 | 0 |  | 0 | 0 | 848100 | 16630 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
913 | Permitting and Engineering (5%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 466500 | 0 | 1 | 0 |  | 0 | 0 | 466500 | 9150 | 1 | - Soft Cost | - Permitting and Engineering
914 | Overall Repair of the Facility | Samandra - Warehouse | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 1650 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 825000 | 16180 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
915 | Contingencies (10%) | Samandra - Warehouse | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 82500 | 0 | 1 | 0 |  | 0 | 0 | 82500 | 1620 | 1 | - Contingencies | 10% contingencies
916 | Preliminaries (10%) | Samandra - Warehouse | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
917 | Permitting and Engineering (5%) | Samandra - Warehouse | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 50000 | 0 | 1 | 0 |  | 0 | 0 | 50000 | 990 | 1 | - Soft Cost | - Permitting and Engineering
918 | Overall Repair of the Facility | Samandra - Shop B | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
919 | Contingencies (10%) | Samandra - Shop B | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 25000 | 0 | 1 | 0 |  | 0 | 0 | 25000 | 500 | 1 | - Contingencies | 10% contingencies
920 | Preliminaries (10%) | Samandra - Shop B | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27500 | 0 | 1 | 0 |  | 0 | 0 | 27500 | 540 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
921 | Permitting and Engineering (5%) | Samandra - Shop B | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 15200 | 0 | 1 | 0 |  | 0 | 0 | 15200 | 300 | 1 | - Soft Cost | - Permitting and Engineering
922 | Overall Repair of the Facility | Samandra - Container Shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2300 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1150000 | 22550 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
923 | Contingencies (10%) | Samandra - Container Shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 115000 | 0 | 1 | 0 |  | 0 | 0 | 115000 | 2260 | 1 | - Contingencies | 10% contingencies
924 | Preliminaries (10%) | Samandra - Container Shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 126500 | 0 | 1 | 0 |  | 0 | 0 | 126500 | 2490 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
925 | Permitting and Engineering (5%) | Samandra - Container Shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 69600 | 0 | 1 | 0 |  | 0 | 0 | 69600 | 1370 | 1 | - Soft Cost | - Permitting and Engineering
926 | Repair of GI Roof | Catering Center | Roof | NY | Navy | Roof | Roof | Navy | 2006 | 5276 |  | m2 | 3 | 3 | 1 | 5 | 0.3 | 2800 | 50 | 1 | 0 |  | 0 | 0 | 4431840 | 86900 | 1 | Water Leak marks were observed in some areas of the building | - Replacements of sections of roofs in catering center
926 | Repair of GI Roof | Catering Center | Roof | NY | Navy | Roof | Roof | Navy | 2006 | 5276 |  | m2 | 0 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 10 |  | 1 | 130390 | 0 | 0 | 0 | - From our thorough study, GI Roof Has a life expectancy of 40 to 70 yrs | - No Capex will be allocated to Phase 2
927 | Replacement of Ceiling Boards | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6186 |  | m2 | 4 | 2 | 1 | 5 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 3711600 | 72780 | 1 | - Sections of the ceiling boards observed water stains | - Replacement of this ceiling boards are necessary - This can be replaced after a year up to life span. Life expentancy of ceiling boards is up to 15yrs-20yrs
927 | Replacement of Ceiling Boards | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6186 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 3711600 | 72780 | 1 | - Sections of the ceiling boards observed water stains | - Replacement of this ceiling boards are necessary - This can be replaced after a year up to life span. Life expentancy of ceiling boards is up to 15yrs-20yrs
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 4 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 1 |  | 1 | 74900 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years - Repair can still be moved to any year | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 11 |  | 0 | 0 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 21 |  | 0 | 0 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
929 | Replacement of wall tiles | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 4258.8 |  | m2 | 4 | 3 | 1 | 5 | 0.2 | 1500 | 50 | 1 | 0 |  | 0 | 0 | 1277640 | 25060 | 1 | -Sections of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
930 | Replacement of floor tiles | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6300 |  | m2 | 4 | 3 | 1 | 5 | 0.3 | 1500 | 50 | 1 | 0 |  | 0 | 0 | 2835000 | 55590 | 1 | -20% of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 50653200 | 15 | 0 | 5 |  | 1 | 993200 | 0 | 0 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. - Replacement of chillers are distributed every 2 years | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 2 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 4 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 5 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 17 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 19 |  | 0 | 0 | 8000000 | 156870 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 20 |  | 0 | 0 | 8000000 | 156870 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
932 | Rehabilitation of storm drainage, HVAC drainage and wastewater drainage system | Catering Center | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2006 | 6186 |  | m2 | 3 | 2 | 1 | 1 | 0.5 | 500 | 0 | 1 | 3 |  | 1 | 83800 | 1546500 | 30330 | 1 | - Clogging Iin the drainage systems were foreseen due to the exposure of waste coming from the kitchen (e.g. oils, foods and etc.). Water leakage was also observed at the area due to the dispense from Condensate Water Pipes. | - Rehabilitation of Pipe network for HVAC, Storm and Waste water.
933 | Fire Suppression System | Catering Center | Lot | NY | Navy | Fire Protection System | Fire Protection | Navy | 2006 | 1 |  | lot | 3 | 1 | 1 | 1 | 1 | 12214500 | 0 | 0 | 0 |  | 1 | 239500 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
934 | Electrical Panel Boards | Catering Center | Lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 838950 | 25 | 1 | 11 |  | 1 | 16450 | 838950 | 16450 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
935 | Miscellaneous items | Catering Center | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1932800 | 0 | 1 | 0 |  | 0 | 10000 | 1932800 | 37900 | 1 | Miscellaneous item includes: - Lack of fire extinguishers - lack of fire signages - missing switch cover - doors - defective toilet fixtures - joinery, sealants - Dirty tiles and walls - Unused equipment - Dirty AC blowers | - Provision of new switch cover - Replacement of doors - Replacement of toilet fixtures, water closets and lavatories - Joinery works - Cleaning, Hauling and Disposal - Cleaning and repair of AC blowers
936 | Contingencies (10%) | Catering Center | Lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4058800 | 0 | 1 | 0 |  | 0 | 0 | 4058800 | 79590 | 1 | - Contingencies | 10% contingencies
937 | Preliminaries (10%) | Catering Center | Lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 4464700 | 0 | 1 | 0 |  | 0 | 0 | 4464700 | 87550 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
938 | Permitting and Engineering (5%) | Catering Center | Lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2455600 | 0 | 1 | 0 |  | 0 | 0 | 2455600 | 48150 | 1 | - Soft Cost | - Permitting and Engineering
939 | Upgrade to comply current structural code | T-BHD Shelter | lot | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2008 | 11430 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 662310 | 11430000 | 224120 | 2 | - The building was constructed in 2008 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
940 | Replacement of polycarbornate Roof and Wall | T-BHD Shelter | lot | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2008 | 11430 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 228600 | 4490 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
940 | Replacement of polycarbornate Roof and Wall | T-BHD Shelter | lot | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2008 | 11430 |  | m2 | 0 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 110390 | 4572000 | 89650 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
941 | Panel Boards | T-BHD Shelter | lot | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1577940 | 25 | 0 | 11 |  | 1 | 30940 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
942 | Gas port/ Electrical Panel Location Provision of Barricade | T-BHD Shelter | lot | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2632500 | 25 | 0 | 2 |  | 1 | 540300 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
942 | Gas port/ Electrical Panel Location Provision of Barricade | T-BHD Shelter | lot | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2632500 | 25 | 1 | 0 |  | 1 |  | 2632500 | 51620 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
943 | Miscellaneous Items | T-BHD Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2008 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 1165900 | 0 | 1 | 0 |  | 1 | 16400 | 1165900 | 22870 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
944 | Contingencies (10%) | T-BHD Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1545700 | 0 | 1 | 0 |  | 0 | 0 | 1545700 | 30310 | 1 | - Contingencies | 10% contingencies
945 | Preliminaries (10%) | T-BHD Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 1700300 | 0 | 1 | 0 |  | 0 | 0 | 1700300 | 33340 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
946 | Permitting and Engineering (5%) | T-BHD Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 935200 | 0 | 1 | 0 |  | 0 | 0 | 935200 | 18340 | 1 | - Soft Cost | - Permitting and Engineering
947 | Upgrade to comply current structural code | Welding Shop (B) | lot | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 10600 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 329870 | 10600000 | 207850 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
948 | Replacement of polycarbornate Roof and Wall | Welding Shop (B) | lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10600 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 636000 | 12480 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
948 | Replacement of polycarbornate Roof and Wall | Welding Shop (B) | lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10600 |  | m2 | 0 | 1 | 1 | 8 | 0.3 | 2000 | 25 | 1 | 14 |  | 1 | 54890 | 6360000 | 124710 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
949 | Panel Boards | Welding Shop (B) | lot | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1577940 | 25 | 0 | 14 |  | 1 | 15470 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
950 | Gas port/ Electrical Panel Location Provision of Barricade | Welding Shop (B) | lot | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2600000 | 25 | 0 | 2 |  | 1 | 269490 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
950 | Gas port/ Electrical Panel Location Provision of Barricade | Welding Shop (B) | lot | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2600000 | 25 | 1 | 0 |  | 1 |  | 2600000 | 50990 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
951 | Miscellaneous Items | Welding Shop (B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 1123600 | 0 | 1 | 0 |  | 0 | 0 | 1123600 | 22040 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
952 | Contingencies (10%) | Welding Shop (B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1496000 | 0 | 1 | 0 |  | 0 | 0 | 1496000 | 29340 | 1 | - Contingencies | 10% contingencies
953 | Preliminaries (10%) | Welding Shop (B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 1645600 | 0 | 1 | 0 |  | 0 | 0 | 1645600 | 32270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
954 | Permitting and Engineering (5%) | Welding Shop (B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 905100 | 0 | 1 | 0 |  | 0 | 0 | 905100 | 17750 | 1 | - Soft Cost | - Permitting and Engineering
955 | Slope Protection | Slope protection | lot | SY | Tenant 3 | Environmental | Structural | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 2550000 | 0 | 1 | 0 |  | 1 | 50000 | 2550000 | 50000 | 2 | - From environmental observation, landslide is prone in the area. Proper protection against landllide is needed. | - Construction of landslide protection
955 | Slope Protection | Slope protection | lot | SY | Tenant 3 | Environmental | Structural | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1530000 | 0 | 1 | 5 |  | 1 | 30000 | 1530000 | 30000 | 2 | - Maintenance of slope protection | - Maintenance of slope protection
956 | Miscellaneous Items | Slope protection | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 255000 | 0 | 1 | 0 |  | 0 | 0 | 255000 | 5000 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
957 | Contingencies (10%) | Slope protection | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 433500 | 0 | 1 | 0 |  | 0 | 0 | 433500 | 8500 | 1 | - Contingencies | 10% contingencies
958 | Preliminaries (10%) | Slope protection | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 476900 | 0 | 1 | 0 |  | 0 | 0 | 476900 | 9360 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
959 | Permitting and Engineering (5%) | Slope protection | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 262300 | 0 | 1 | 0 |  | 0 | 0 | 262300 | 5150 | 1 | - Soft Cost | - Permitting and Engineering
960 | Spill Prevention Kits Tenant 3 | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Environmental | Environmental | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
961 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
962 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
963 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
964 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
965 | Spill Prevention Kits Austal | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Environmental | Environmental | Austal | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
966 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
967 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
968 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
969 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
970 | Spill Prevention Kits Dock 6 | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Environmental | Environmental | Dock 6 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
971 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
972 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
973 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
974 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
975 | Spill Prevention Kits Navy | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Environmental | Environmental | Navy | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
976 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
977 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
978 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
979 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
980 | Upgrade to comply current structural code | Nagyantok Material Store and Bond shop | Lot | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2017 | 9850 |  | m2 | 3 | 2 | 0 | 1 | 1 | 4000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - No Capex will be allocated to Phase 2
981 | Overall Repair of the Facility | Nagyantok Material Store and Bond shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | Miscellaneous item includes: - damaged rubberized paint - buckled roof purlins - observed minor damages in roofing | Miscellaneous item includes: - repainting of slab with rubberized paint - repair of purlins - replacement of roof sheets - cleaning
982 | Contingencies (10%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 25000 | 0 | 1 | 0 |  | 0 | 0 | 25000 | 500 | 1 | - Contingencies | 10% contingencies
983 | Preliminaries (10%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27500 | 0 | 1 | 0 |  | 0 | 0 | 27500 | 540 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
984 | Permitting and Engineering (5%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 15200 | 0 | 1 | 0 |  | 0 | 0 | 15200 | 300 | 1 | - Soft Cost | - Permitting and Engineering
985 | Overall Repair of the Facility | Nagyantok Procurement Storage shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2100 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1050000 | 20590 | 1 | Miscellaneous item includes: - rusted purlins and other structural members - damaged purlins | Miscellaneous item includes: - repainting of rusted members - repair of purlins - cleaning
986 | Contingencies (10%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105000 | 0 | 1 | 0 |  | 0 | 0 | 105000 | 2060 | 1 | - Contingencies | 10% contingencies
987 | Preliminaries (10%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 115500 | 0 | 1 | 0 |  | 0 | 0 | 115500 | 2270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
988 | Permitting and Engineering (5%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 63600 | 0 | 1 | 0 |  | 0 | 0 | 63600 | 1250 | 1 | - Soft Cost | - Permitting and Engineering
989 | Overall Repair of the Facility | Nagyantok Segragation Area | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1250000 | 24510 | 1 | Miscellaneous item includes: - rusted purlins and other structural members - damaged purlins | Miscellaneous item includes: - repainting of rusted members - repair of purlins - cleaning
990 | Contingencies (10%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 125000 | 0 | 1 | 0 |  | 0 | 0 | 125000 | 2460 | 1 | - Contingencies | 10% contingencies
991 | Preliminaries (10%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 137500 | 0 | 1 | 0 |  | 0 | 0 | 137500 | 2700 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
992 | Permitting and Engineering (5%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 75700 | 0 | 1 | 0 |  | 0 | 0 | 75700 | 1490 | 1 | - Soft Cost | - Permitting and Engineering
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 4 | 1 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
994 | Upgrade to comply current structural code | Guest House | Lot | NY | Navy | Structural Upgrade | Structural | Navy | 2008 | 2870 |  | m2 | 3 | 3 | 0 | 4 | 1 | 4000 | 0 | 0.5 | 0 |  | 1 | 220670 | 5740000 | 112550 | 2
995 | Replacement of wall tiles | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 800 |  | m2 | 4 | 3 | 1 | 5 | 1 | 1500 | 50 | 1 | 0 |  | 1 | 96400 | 1200000 | 23530 | 1 | -Section of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
996 | Replacement of floor tiles | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2610 |  | m2 | 4 | 3 | 1 | 5 | 1 | 1500 | 50 | 1 | 0 |  | 1 | 126800 | 3915000 | 76770 | 1 | -20% of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
997 | HVAC System | Guest House | Lot | NY | Navy | HVAC | Mechanical | Navy | 2008 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 5 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
997 | HVAC System | Guest House | Lot | NY | Navy | HVAC | Mechanical | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 20 |  | 1 | 466700 | 8000000 | 156870 | 2 | - life expectancy of chillers | - Replacement of chillers
998 | Fire Suppression System | Guest House | Lot | NY | Navy | Fire Protection System | Fire Protection | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 5737500 | 0 | 0 | 0 |  | 1 | 112500 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
999 | Replacement of Ceiling Boards | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2870 |  | lot | 4 | 3 | 1 | 5 | 1 | 720 | 15 | 1 | 0 |  | 1 | 101400 | 2066400 | 40520 | 1 | - water stains are found on the ceiling boards - ceiling boards are deteriorated due to water stains | - Replacement of ceiling boards
999 | Replacement of Ceiling Boards | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2870 |  | lot | 0 | 1 | 1 | 8 | 1 | 720 | 15 | 1 | 15 |  | 1 | 101400 | 2066400 | 40520 | 1 | - water stains are found on the ceiling boards - ceiling boards are deteriorated due to water stains | - Replacement of ceiling boards
1000 | Replacement of Roof | Guest House | Lot | NY | Navy | Roof | Roof | Navy | 2008 | 2870 |  | lot | 4 | 3 | 1 | 4 | 1 | 2800 | 50 | 1 | 0 |  | 1 | 177900 | 8036000 | 157570 | 1 | - According to Hanjin, roofs were damaged due to earthquake - water stains found inside the building due to damaged roof | - replacement of roofs
1001 | Electrical Panel Boards | Guest House | Lot | NY | Navy | Electrical System | Electrical | Navy | 2008 | 1 |  | lot | 4 | 2 | 1 | 5 | 1 | 199920 | 25 | 1 | 11 |  | 1 | 3920 | 199920 | 3920 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
1002 | Miscellaneous items | Guest House | Lot | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2927300 | 0 | 1 | 0 |  | 0 | 19900 | 2927300 | 57400 | 1 | Miscellaneous item includes: - Lack of fire extinguishers - lack of fire signages - missing switch cover - doors - defective toilet fixtures - joinery, sealants - Dirty tiles and walls - Unused equipment - Dirty AC blowers - dilapidated wooden trellis - Damaged Glass wall | - Provision of new switch cover - Replacement of doors - Replacement of toilet fixtures, water closets and lavatories - Joinery works - Cleaning, Hauling and Disposal - Cleaning and repair of AC blowers - Resotration of wooden trellis - Replacement of Glass
1003 | Contingencies (10%) | Guest House | Lot | SY | Navy | Contingencies | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3220000 | 0 | 1 | 0 |  | 0 | 0 | 3220000 | 63140 | 1 | - Contingencies | 10% contingencies
1004 | Preliminaries (10%) | Guest House | Lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3542000 | 0 | 1 | 0 |  | 0 | 0 | 3542000 | 69460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1005 | Permitting and Engineering (5%) | Guest House | Lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1948100 | 0 | 1 | 0 |  | 0 | 0 | 1948100 | 38200 | 1 | - Soft Cost | - Permitting and Engineering
1006 | Shared Utilities - Electricity | Shared Utilities - Electricity | Lot | NY+SY | JV | Electrical System | Electrical | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 4 | 1 | 1504500 | 0 | 1 | 0 |  | 0 | 0 | 1504500 | 29500 | 3 | - Outdated software | - Software replacement
1007 | Contingencies (10%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150500 | 0 | 1 | 0 |  | 0 | 0 | 150500 | 2960 | 3 | - Contingencies | 10% contingencies
1008 | Preliminaries (10%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165500 | 0 | 1 | 0 |  | 0 | 0 | 165500 | 3250 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1009 | Permitting and Engineering (5%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 91100 | 0 | 1 | 0 |  | 0 | 0 | 91100 | 1790 | 3 | - Soft Cost | - Permitting and Engineering
1010 | Shared Utilities - Water | Shared Utilities - Water | Lot | NY+SY | JV | Plumbing System | Civil | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 4 | 1 | 5253000 | 0 | 1 | 0 |  | 0 | 0 | 5253000 | 103000 | 3 | - Intallation of water meters | - Intallation of water meters
1011 | Contingencies (10%) | Shared Utilities - Water | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 525300 | 0 | 1 | 0 |  | 0 | 0 | 525300 | 10300 | 3 | - Contingencies | 10% contingencies
1012 | Preliminaries (10%) | Shared Utilities - Water | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 577900 | 0 | 1 | 0 |  | 0 | 0 | 577900 | 11340 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1013 | Permitting and Engineering (5%) | Shared Utilities - Water | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 317900 | 0 | 1 | 0 |  | 0 | 0 | 317900 | 6240 | 3 | - Soft Cost | - Permitting and Engineering
1014 | Shared Utilities - Fence | Shared Utilities - Fence | Lot | NY+SY | JV | Perimeter Fence | Civil | Shared | 2020 | 9100 |  | lm | 0 | 1 | 1 | 6 | 1 | 30000 | 0 | 1 | 0 |  | 0 | 0 | 273000000 | 5352950 | 3 | - Construction of perimeter fence | - Construction of perimeter fence
1015 | Contingencies (10%) | Shared Utilities - Fence | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27300000 | 0 | 1 | 0 |  | 0 | 0 | 27300000 | 535300 | 3 | - Contingencies | 10% contingencies
1016 | Preliminaries (10%) | Shared Utilities - Fence | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 30030000 | 0 | 1 | 0 |  | 0 | 0 | 30030000 | 588830 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1017 | Permitting and Engineering (5%) | Shared Utilities - Fence | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 16516500 | 0 | 1 | 0 |  | 0 | 0 | 16516500 | 323860 | 3 | - Soft Cost | - Permitting and Engineering

## tidycapex
No | CAPEXassets | Facilities | FloorLevel | Area | Tenant | WorkType | Disciplines | User | YearBuilt | Quantity | TenantQ | Unit | States | Risk | CodeComply | InteType | IntePec | UnitCost | LifeSpan | Prob | InterYear | TenantInterYear | IncludedPhase1 | NPVCAPEXP1USD | NPVCapexP2Php | NPVCapexUSD | ReturntoAs-built | ReasonsforIntervention | Scopes
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 |  | 126000 | 2480 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and delapidated | -Re-application of Rubberized flooring to as-built condition
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy
1 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 1 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 |  | 126000 | 2480 | 1 | - Rubberized paint of the 1st floor is already peeled-off and delapidated | -Re-application of Rubberized flooring to as-built condition
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
2 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 13 | 1 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 |  | 126000 | 2480 | 1 | - life expectancy of paints | -Re-application of Rubberized flooring to as-built due to life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 2 |  | 1 | 18500 | 315000 | 6180 | 0 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 12 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
3 | Repainting of Walls 2nd Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 22 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 2 |  | 0 | 0 | 315000 | 6180 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 12 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
4 | Repainting of Walls 1st Floor | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 22 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 3 | 1 | 5 | 0.2 | 720 | 15 | 1 | 0 |  | 0 |  | 60480 | 1190 | 1 | - sections of the ceiling boards are damaged and sagging | - Replacement of new ceiling board to retain its as-built condition
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 5 | 1 | 720 | 15 | 1 | 7 |  | 0 |  | 302400 | 5930 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards due to life expectancy
5 | Replacement of Ceiling Boards | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 420 |  | m2 | 0 | 1 | 1 | 8 | 1 | 720 | 15 | 1 | 22 |  | 0 |  | 302400 | 5930 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards due to life expectancy
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 4 | 3 | 1 | 5 | 1 | 140000 | 10 | 1 | 0 |  | 0 |  | 280000 | 5500 | 1 | - According to the operator of this field office, the floor mounted AC is not in good condition. - Needs to be checked and tested since it is not operated after the shipyard operation | - Option to replace the floor mounted AC's if found these cannot be repaired.
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 10 |  | 0 |  | 280000 | 5500 | 1 | - life expectancy of HVAC | - Installation of new Air-condition units due to life expectancy
6 | Replacement floor mounted AC | Field Office 13 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2012 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 20 |  | 0 |  | 280000 | 5500 | 1 | - life expectancy of HVAC | - Installation of new Air-condition units due to life expectancy
7 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 13 | 2 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 6 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 420000 | 8240 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
8 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 13 | 2 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 420 |  | m2 | 3 | 2 | 1 | 6 | 1 | 2000 | 25 | 1 | 0 |  | 0 |  | 840000 | 16480 | 2 | - All auxiliary wires are in fair condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
9 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 13 | 2 | NY | Navy | Interior | Architectural | Navy | 2012 | 40 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 80000 | 1570 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
10 | Repair of roofs and gutters | Field Office 13 | Lot | NY | Navy | Roof | Roof | Navy | 2012 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 1 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
11 | Provision for the storm drainage | Field Office 13 | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2012 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 3500 | 0 | 1 | 0 |  | 0 | 0 | 525000 | 10300 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
12 | Miscellaneous items | Field Office 13 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 308748 | 0 | 1 | 0 |  | 0 | 0 | 308748 | 6060 | 1 | - Allocation for the unforeseen repair/installation such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace
13 | Contingencies (10%) | Field Office 13 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 339700 | 0 | 1 | 0 |  | 0 | 0 | 339700 | 6670 | 1 | - Contingencies | 10% contingencies
14 | Preliminaries (10%) | Field Office 13 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 373600 | 0 | 1 | 0 |  | 0 | 0 | 373600 | 7330 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
15 | Permitting and Engineering (5%) | Field Office 13 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192900 | 0 | 1 | 0 |  | 0 | 0 | 192900 | 3790 | 1 | - Soft Cost | - Permitting and Engineering
16 | Panel Boards | Sub Station #33 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
17 | Transformers repair | Sub Station #33 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
18 | Overall Repair of the facility | Sub Station #33 | 1 | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 685 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 685000 | 13440 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
19 | Contingencies (10%) | Sub Station #33 | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 118500 | 0 | 1 | 0 |  | 0 | 0 | 118500 | 2330 | 1 | - Contingencies | 10% contingencies
20 | Preliminaries (10%) | Sub Station #33 | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 130400 | 0 | 1 | 0 |  | 0 | 0 | 130400 | 2560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
21 | Permitting and Engineering (5%) | Sub Station #33 | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 71700 | 0 | 1 | 0 |  | 0 | 0 | 71700 | 1410 | 1 | - Soft Cost | - Permitting and Engineering
22 | Installation of missing X- Brace | Pipe Manufacture Shop A&B | 1 | NY | Navy | Structural Elements | Structural | Navy | 2011 | 313860 |  | kg | 4 | 3 | 1 | 5 | 0.03 | 200 | 0 | 1 | 0 |  | 0 | 0 | 1883160 | 36930 | 1 | - some cross braces are already missing and already experiencing buckling and sagging | - Repair and installation of replacement of X-Braces
23 | Panel Boards | Pipe Manufacture Shop A&B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 721140 | 25 | 0 | 11 |  | 1 | 14140 | 0 | 0 | 1 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
24 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Pipe Manufacture Shop A&B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 70000 | 25 | 1 | 11 |  | 0 | 0 | 7140000 | 140000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
25 | Replacement of polycarbornate Roof | Pipe Manufacture Shop A&B | 1 | NY | Navy | Roof | Roof | Navy | 2011 | 8640 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 16 |  | 0 | 0 | 17280000 | 338830 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
26 | Upgrade to comply current structural code | Pipe Manufacture Shop A&B | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2011 | 10462 |  | m2 | 3 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.1 | 0 |  | 1 | 905370 | 4184800 | 82060 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
27 | Gas port/ Electrical Panel Location Provision of Barricade | Pipe Manufacture Shop A&B | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2011 | 1 |  | lot | 3 | 3 | 1 | 6 | 1 | 600000 | 25 | 0 | 2 |  | 1 | 246165 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
27 | Gas port/ Electrical Panel Location Provision of Barricade | Pipe Manufacture Shop A&B | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2011 | 1 |  | lot | 3 | 3 | 1 | 6 | 1 | 600000 | 25 | 1 | 0 |  | 1 |  | 600000 | 11770 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
28 | Miscellaneous Items | Pipe Manufacture Shop A&B | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 606800 | 0 | 1 | 0 |  | 0 | 0 | 606800 | 11900 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
29 | Contingencies (10%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 727500 | 0 | 1 | 0 |  | 0 | 0 | 727500 | 14270 | 1 | - Contingencies | 10% contingencies
30 | Preliminaries (10%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 800300 | 0 | 1 | 0 |  | 0 | 0 | 800300 | 15700 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
31 | Permitting and Engineering (5%) | Pipe Manufacture Shop A&B | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 440200 | 0 | 1 | 0 |  | 0 | 0 | 440200 | 8640 | 1 | - Soft Cost | - Permitting and Engineering
32 | Panel Boards | Shelter for Piping | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 4808790 | 25 | 0 | 11 |  | 1 | 94290 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
33 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Shelter for Piping | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 0 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
34 | Fire Suppression System | Shelter for Piping | 1 | NY | Navy | Fire Protection System | Fire Protection | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 12217050 | 0 | 0 | 0 |  | 1 | 239500 | 0 | 0 | 0 | - During our detailed inspection,this building is only for the storage of pipe and other appurtenences. Hence, current fire extinguishing set-up is okay | - No Capex will be allocated to Phase 2
35 | Repair of deformed Structural steel frame | Shelter for Piping | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 1 |  | lot | 4 | 3 | 1 | 3 | 1 | 5793600 | 0 | 0 | 0 |  | 1 | 113600 | 0 | 0 | 0 | - During our detailed inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
36 | Upgrade to comply current structural code | Shelter for Piping | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 2090 |  | m2 | 3 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.1 | 0 |  | 1 | 166400 | 836000 | 16400 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
37 | Miscellaneous Items | Shelter for Piping | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - repainting of rusted structural steel members - poor condition of electrical wires | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Repair/Installation of missing cross braces - Replacement of dilapidated electrical wrings - Repainting of rusted structural member frames
38 | Contingencies (10%) | Shelter for Piping | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92000 | 0 | 1 | 0 |  | 0 | 0 | 92000 | 1810 | 1 | - Contingencies | 10% contingencies
39 | Preliminaries (10%) | Shelter for Piping | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 101200 | 0 | 1 | 0 |  | 0 | 0 | 101200 | 1990 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
40 | Permitting and Engineering (5%) | Shelter for Piping | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 55700 | 0 | 1 | 0 |  | 0 | 0 | 55700 | 1100 | 1 | - Soft Cost | - Permitting and Engineering
41 | Demolition and Debris Removal of CO2 Plant | CO2 Plant | 1 | NY | Navy | Demolition | Building | Navy | 2006 | 1200 |  | m2 | 5 | 3 | 1 | 1 | 1 | 3800 | 0 | 1 | 10 |  | 0 |  | 4560000 | 89420 | 3 | - The CO2 plant is in very poor condition. - all structural members are rusted - Roofs are dilapidated | - Cerberus/Tenant to give additional instruction of the future usage of the building
42 | Contingencies (10%) | CO2 Plant | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 10 |  | 0 | 0 | 83600 | 1640 | 1 | - Contingencies | 10% contingencies
43 | Preliminaries (10%) | CO2 Plant | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92000 | 0 | 1 | 10 |  | 0 | 0 | 92000 | 1810 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
44 | Permitting and Engineering (5%) | CO2 Plant | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4600 | 0 | 1 | 10 |  | 0 | 0 | 4600 | 100 | 1 | - Soft Cost | - Permitting and Engineering
45 | Overall structural retrofitting | Piping Pre-treatment building Galva | 1 | NY | Navy | Structural Elements | Structural | Navy | 2011 | 2900 |  | m2 | 5 | 3 | 1 | 3 | 0.7 | 5000 | 0 | 1 | 0 |  | 1 | 166400 | 10150000 | 199020 | 1 | - The Galvanizing is in bad condition and needs to be retrofitted immediately. Steel frames are rusted and requires major removal of rust. | - full rehabilitation of structural elements including replacement of rusted steel elements
46 | Replacement of rusted GI wall sheet | Piping Pre-treatment building Galva | 1 | NY | Navy | Building Fabric | Architectural | Navy | 2011 | 3000 |  | m2 | 5 | 3 | 1 | 3 | 0.8 | 2500 | 0 | 1 | 0 |  | 1 | 248625 | 6000000 | 117650 | 1 | - Sections of the façade are rusted and needs to be replaced | -replacement of GI sheet façade
47 | Replacement of GI roofing including insulation | Piping Pre-treatment building Galva | 1 | NY | Navy | Roof | Roof | Navy | 2011 | 3200 |  | m2 | 5 | 3 | 1 | 3 | 0.8 | 2800 | 0 | 1 | 0 |  | 1 | 464000 | 7168000 | 140550 | 1 | - Sections of the façade are rusted and needs to be replaced | - replacement of GI sheet roof
48 | Replacement of all electrical wirings | Piping Pre-treatment building Galva | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 2900 |  | m2 | 5 | 3 | 1 | 3 | 1 | 4000 | 50 | 1 | 0 |  | 1 | 208000 | 11600000 | 227460 | 1 | - all electrical wirings need to be replaced due to the previous facility usage. | - Replacement of electrical wirings and cables
48 | Replacement of all electrical wirings | Piping Pre-treatment building Galva | 1 | NY | Navy | Electrical System | Electrical | Navy | 2011 | 2900 |  | m2 | 0 | 3 | 1 | 8 | 1 | 4000 | 50 | 0 | 25 |  | 1 | 145600 | 0 | 0 | 0 | - due to the change of usage, service life of the electrical wires will be further extended to its maximum life expectancy | - No CapEx will be included in Phase 2
49 | New Protective Coating | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 1 |  | lot | 5 | 3 | 1 | 4 | 1 | 2565300 | 0 | 1 | 0 |  | 1 | 50300 | 2565300 | 50300 | 1 | - most columns are rusted; however, can still be used and only needs to be rehabilitated by removing the rust and apply new protective coating | - Repainting of rusted structural steel to protect the steel from re-rusting
50 | Replacement of sliding door (7mx9m) | Piping Pre-treatment building Galva | 1 | NY | Navy | Building Fabric | Architectural | Navy | 2011 | 2 |  | unit | 5 | 3 | 1 | 5 | 1 | 540000 | 0 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Sliding door is already damaged - rollers are rusted and are stocked in one place | - total replacement of sliding doors
51 | Filling and concreting (200mm) of tanks | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 420 |  | m3 | 0 | 3 | 1 | 6 | 1 | 700 | 0 | 1 | 0 |  | 0 | 0 | 294000 | 5770 | 3 | - Philippine Navy will change the current usage of the building | - Filling and concreting of the galvanizing tanks to suit PN requirement
52 | Rehabiltation of control room for the gantry of the Crane/hoist (PN Navy admin bldg and Control room) | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 50 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 100000 | 1970 | 3 | - The current usage of the area is for the control room of the gantry. - Philippine navy plans to keep the room as a admin building | - Rehabilitation of the room to comply with admin building; - Repainting of Walls - Rubberized floorings - Replacement of damaged ceilings
53 | Warehouse Building - Damage Ceiling | Piping Pre-treatment building Galva | 1 | NY | Navy | Interior | Architectural | Navy | 2011 | 140 |  | m2 | 5 | 3 | 1 | 5 | 1 | 720 | 15 | 1 | 0 |  | 0 | 0 | 100800 | 1980 | 1 | - Ceiling is damage due to earthquake | - Replacement of ceiling
54 | Miscellaneous Items | Piping Pre-treatment building Galva | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2011 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1953000 | 0 | 1 | 0 |  | 0 | 0 | 1953000 | 38300 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal
55 | Contingencies (10%) | Piping Pre-treatment building Galva | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4101200 | 0 | 1 | 0 |  | 0 | 0 | 4101200 | 80420 | 1 | - Contingencies | 10% contingencies
56 | Preliminaries (10%) | Piping Pre-treatment building Galva | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4511300 | 0 | 1 | 0 |  | 0 | 0 | 4511300 | 88460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
57 | Permitting and Engineering (5%) | Piping Pre-treatment building Galva | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2011 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2481200 | 0 | 1 | 0 |  | 0 | 0 | 2481200 | 48660 | 1 | - Soft Cost | - Permitting and Engineering
58 | Repair of Missing 12mm Dia Rod Brace including accessories | Painting Shop A -1 | 1 | NY | Navy | Structural Elements | Structural | Navy | 2006 | 60 |  | kg | 5 | 3 | 1 | 5 | 1 | 200 | 0 | 1 | 0 |  | 0 | 0 | 12000 | 240 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
59 | Upgrade to comply current structural code | Painting Shop A -1 | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 860 |  | kg | 3 | 1 | 0 | 1 | 1 | 4000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2
60 | Replacement of GI Roof | Painting Shop A -1 | 1 | NY | Navy | Roof | Roof | Navy | 2006 | 860 |  | m2 | 5 | 3 | 1 | 2 | 0.5 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 1075000 | 21080 | 1 | - Most roofs are already rusted | - replacement of GI sheet roof
61 | Replacement of all electrical wirings | Painting Shop A -1 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 860 |  | m2 | 0 | 3 | 1 | 8 | 1 | 2500 | 25 | 1 | 11 |  | 0 | 0 | 2150000 | 42160 | 1 | - All electrical system are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement at end of life of conduit, wirings, electrical equipments such as lighting fixtures & wiring devices
62 | Miscellaneous Items | Painting Shop A -1 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 108700 | 0 | 1 | 0 |  | 0 | 0 | 108700 | 2140 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - Missing 12mm Dia Rod Brace including accessories - Removal of paint cavities - Broken Door Jambs and knobs | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal - Installation of missing 12mm dia rod brace - Replacement of door Jambs and knobs - Repainting of rusted steel members
63 | Contingencies (10%) | Painting Shop A -1 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 119600 | 0 | 1 | 0 |  | 0 | 0 | 119600 | 2350 | 1 | - Contingencies | 10% contingencies
64 | Preliminaries (10%) | Painting Shop A -1 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 131600 | 0 | 1 | 0 |  | 0 | 0 | 131600 | 2590 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
65 | Permitting and Engineering (5%) | Painting Shop A -1 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 72400 | 0 | 1 | 0 |  | 0 | 0 | 72400 | 1420 | 1 | - Soft Cost | - Permitting and Engineering
66 | Replacement of mechanical louvers and insulation pads | Piping Shelter | 1 | NY | Navy | Mechanical System | Mechanical | Navy | 2012 | 1 |  | lot | 4 | 2 | 1 | 5 | 0.5 | 800000 | 0 | 1 | 2 |  | 0 | 0 | 400000 | 7850 | 1 | - louvers and insulation pads are damaged. | - replacement of louvers and insulation pads to retain its as-built condition - can still be used until 2 years
67 | Replacement of all electrical wirings | Piping Shelter | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 1000 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2500 | 25 | 1 | 17 |  | 0 |  | 2500000 | 49020 | 1 | - All electrical system are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement at end of life of conduit, wirings, electrical equipments such as lighting fixtures & wiring devices
68 | Upgrade to comply current structural code | Piping Shelter | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 0 | 1 | 1 | 4000 | 0 | 0.1 | 0 |  | 0 |  | 400000 | 7850 | 2 | -The building was constructed in 2011 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
69 | Miscellaneous items | Piping Shelter | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 80000 | 0 | 1 | 0 |  | 0 |  | 80000 | 1570 | 1 | Allocation for the unforeseen repair/installation of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - Rusted Steel Frame members - Removal of paint cavities - Damaged Sliding Door Rubber Gasket | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Cleaning of the facility - Hauling and Disposal - Installation of missing 12mm dia rod brace - Repainting of rusted steel members - Replacement of damaged steel gasket
70 | Contingencies (10%) | Piping Shelter | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 88000 | 0 | 1 | 0 |  | 0 | 0 | 88000 | 1730 | 1 | - Contingencies | 10% contingencies
71 | Preliminaries (10%) | Piping Shelter | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 96800 | 0 | 1 | 0 |  | 0 | 0 | 96800 | 1900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
72 | Permitting and Engineering (5%) | Piping Shelter | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 53300 | 0 | 1 | 0 |  | 0 | 0 | 53300 | 1050 | 1 | - Soft Cost | - Permitting and Engineering
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 3 | 3 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 93000 | 1830 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 10 |  | 0 | 0 | 93000 | 1830 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy
73 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 0 | 1 | 1 | 8 | 1 | 300 | 10 | 1 | 20 |  | 0 | 0 | 93000 | 1830 | 1 | - life expectancy of rubberize paints | -Re-application of Rubberized flooring to as-built due to life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 75000 | 1480 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
74 | Repainting of Walls | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 | 0 | 75000 | 1480 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
75 | Replacement of Ceiling Boards | Field Office 14 | 1 | NY | Navy | Interior | Architectural | Navy | 2016 | 310 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 11 |  | 0 | 0 | 186000 | 3650 | 1 | - Ceiling Boards are still in good condition | - Installation of new ceiling boards due to life expectancy
76 | Replacement of DX type units | Field Office 14 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2016 | 16 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 6 |  | 0 | 0 | 2208000 | 43300 | 1 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service
76 | Replacement of DX type units | Field Office 14 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2016 | 16 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 16 |  | 0 | 0 | 2208000 | 43300 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
77 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 14 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 310 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 310000 | 6080 | 2 | - All wires are messed up and are scattered around the places which is a tripping hazard. | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
78 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 14 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 310 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 620000 | 12160 | 2 | - All auxiliary wires are in fair condition but still re-usable - All IT components such as CCTV and ID scanner are in fair condition. -All wires are messed and are scattered around the places which is a tripping hazard. | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
79 | Repair of roofs and gutters | Field Office 14 | Lot | NY | Navy | Roof | Roof | Navy | 2016 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from broken downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
80 | Miscellaneous items | Field Office 14 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 81840 | 0 | 1 | 0 |  | 0 | 0 | 81840 | 1610 | 1 | - Allocation for the unforeseen repair/installation such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Hauling and Disposal of unused appliances and furnitures - Installation of missing cross brace
81 | Contingencies (10%) | Field Office 14 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110500 | 0 | 1 | 0 |  | 0 | 0 | 110500 | 2170 | 1 | - Contingencies | 10% contingencies
82 | Preliminaries (10%) | Field Office 14 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121600 | 0 | 1 | 0 |  | 0 | 0 | 121600 | 2390 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
83 | Permitting and Engineering (5%) | Field Office 14 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66900 | 0 | 1 | 0 |  | 0 | 0 | 66900 | 1320 | 1 | - Soft Cost | - Permitting and Engineering
84 | Generator Set | Main Generator Room | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 7.5 |  | MW | 3 | 1 | 1 | 8 | 1 | 13500000 | 30 | 1 | 15 |  | 0 | 0 | 101250000 | 1985300 | 1 | - Generator has at least 30 years of life expectancy. If properly maintained, this equipment can be prolonged | - Replacement of Generator due to end of life
85 | Overall Repair of the Facility | Main Generator Room | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 75000 | 0 | 1 | 0 |  | 0 | 0 | 75000 | 1480 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages
86 | Contingencies (10%) | Main Generator Room | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 7500 | 0 | 1 | 0 |  | 0 | 0 | 7500 | 150 | 1 | - Contingencies | 10% contingencies
87 | Preliminaries (10%) | Main Generator Room | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 8300 | 0 | 1 | 0 |  | 0 | 0 | 8300 | 170 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
88 | Permitting and Engineering (5%) | Main Generator Room | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4600 | 0 | 1 | 0 |  | 0 | 0 | 4600 | 100 | 1 | - Soft Cost | - Permitting and Engineering
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 5 | 2 | 1 | 3 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
89 | Repainting of walls and ceiling | Barracks - Accommodation | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 166 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 41500 | 820 | 1 | - walls are vandalized and stained | - Repainting of walls
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 60000 | 1180 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 60000 | 1180 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
90 | Replacement of Air-condition unit (Inverter type) | Barracks - Accommodation | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 60000 | 1180 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
91 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - Accommodation | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 70 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 70000 | 1380 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
92 | Miscellaneous Items | Barracks - Accommodation | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 17200 | 0 | 1 | 0 |  | 0 |  | 17200 | 340 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
93 | Contingencies (10%) | Barracks - Accommodation | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 18900 | 0 | 1 | 0 |  | 0 | 0 | 18900 | 380 | 1 | - Contingencies | 10% contingencies
94 | Preliminaries (10%) | Barracks - Accommodation | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 20800 | 0 | 1 | 0 |  | 0 | 0 | 20800 | 410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
95 | Permitting and Engineering (5%) | Barracks - Accommodation | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 11500 | 0 | 1 | 0 |  | 0 | 0 | 11500 | 230 | 1 | - Soft Cost | - Permitting and Engineering
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
96 | Repainting of walls and ceiling | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
97 | Supply and installation of linoleum flooring | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 195000 | 3830 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
97 | Supply and installation of linoleum flooring | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 195000 | 3830 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 5 | 2 | 1 | 5 | 1 | 45000 | 10 | 1 | 0 |  | 0 | 0 | 4815000 | 94420 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 10 |  | 0 | 0 | 4815000 | 94420 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
98 | Replacement of Air-condition unit (Inverter type) | Barracks - C | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 107 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 20 |  | 0 | 0 | 4815000 | 94420 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
99 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - C | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 200 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 400000 | 7850 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
100 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - C | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1300000 | 25500 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
101 | Miscellaneous Items | Barracks - C | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 617800 | 0 | 1 | 0 |  | 0 |  | 617800 | 12120 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
102 | Contingencies (10%) | Barracks - C | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 834100 | 0 | 1 | 0 |  | 0 | 0 | 834100 | 16360 | 1 | - Contingencies | 10% contingencies
103 | Preliminaries (10%) | Barracks - C | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 917500 | 0 | 1 | 0 |  | 0 | 0 | 917500 | 18000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
104 | Permitting and Engineering (5%) | Barracks - C | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 504600 | 0 | 1 | 0 |  | 0 | 0 | 504600 | 9900 | 1 | - Soft Cost | - Permitting and Engineering
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
105 | Repainting of walls and ceiling | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 2490 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 622500 | 12210 | 1 | - walls are vandalized and stained | - Repainting of walls
106 | Supply and installation of linoleum flooring | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 780 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 117000 | 2300 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
106 | Supply and installation of linoleum flooring | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 780 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 117000 | 2300 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 0 | 10 |  | 1 | 489000 | 0 | 0 | 0 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC moved to immediate to retain its as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
107 | Replacement of Air-condition unit (Inverter type) | Barracks - B | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 3150000 | 61770 | 1 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
108 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - B | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 130 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 |  | 260000 | 5100 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
109 | Panel Boards | Barracks - B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 346290 | 25 | 0 | 11 |  | 1 | 6790 | 0 | 0 | 0 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
110 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - B | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 780 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 780000 | 15300 | 1 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
111 | Miscellaneous Items | Barracks - B | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 291200 | 0 | 1 | 0 |  | 0 |  | 291200 | 5710 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
112 | Contingencies (10%) | Barracks - B | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 393100 | 0 | 1 | 0 |  | 0 | 0 | 393100 | 7710 | 1 | - Contingencies | 10% contingencies
113 | Preliminaries (10%) | Barracks - B | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 432400 | 0 | 1 | 0 |  | 0 | 0 | 432400 | 8480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
114 | Permitting and Engineering (5%) | Barracks - B | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 237900 | 0 | 1 | 0 |  | 0 | 0 | 237900 | 4670 | 1 | - Soft Cost | - Permitting and Engineering
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
115 | Repainting of walls and ceiling | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
116 | Supply and installation of linoleum flooring | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 | 0 | 225000 | 4420 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
116 | Supply and installation of linoleum flooring | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 | 0 | 225000 | 4420 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 1 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 1 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
117 | Replacement of Air-condition unit (Inverter type) | Barracks - Admin | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 1 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
118 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - Admin | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 150 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 300000 | 5890 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
119 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - Admin | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
120 | Miscellaneous Items | Barracks - Admin | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 380800 | 0 | 1 | 0 |  |  | 0 | 380800 | 7470 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
121 | Contingencies (10%) | Barracks - Admin | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 514100 | 0 | 1 | 0 |  | 0 | 0 | 514100 | 10090 | 1 | - Contingencies | 10% contingencies
122 | Preliminaries (10%) | Barracks - Admin | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 565500 | 0 | 1 | 0 |  | 0 | 0 | 565500 | 11090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
123 | Permitting and Engineering (5%) | Barracks - Admin | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 311100 | 0 | 1 | 0 |  | 0 | 0 | 311100 | 6100 | 1 | - Soft Cost | - Permitting and Engineering
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
124 | Repainting of walls and ceiling | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
125 | Supply and installation of linoleum flooring | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1100 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 165000 | 3240 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
125 | Supply and installation of linoleum flooring | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 165000 | 3240 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
126 | Replacement of Wooden Flooring to 6mm steel plate | Barracks - G1 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 52250 |  | kg | 0 | 1 | 1 | 8 | 1 | 250 | 20 | 1 | 20 |  | 0 |  | 13062500 | 256130 | 1 | - Wooden floors are already decaying due to termites | - replacement of wooden floors to steel plate.
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 1 |  | 1830000 | 35890 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 |  | 1830000 | 35890 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
127 | Replacement of Air-condition unit (Inverter type) | Barracks - G1 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 61 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 |  | 1830000 | 35890 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
128 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - G1 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1100 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1100000 | 21570 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
129 | Miscellaneous Items | Barracks - G1 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 397000 | 0 | 1 | 0 |  |  | 0 | 397000 | 7790 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of comfort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of comfort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
130 | Contingencies (10%) | Barracks - G1 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 436700 | 0 | 1 | 0 |  | 0 | 0 | 436700 | 8570 | 1 | - Contingencies | 10% contingencies
131 | Preliminaries (10%) | Barracks - G1 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 480400 | 0 | 1 | 0 |  | 0 | 0 | 480400 | 9420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
132 | Permitting and Engineering (5%) | Barracks - G1 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 264300 | 0 | 1 | 0 |  | 0 | 0 | 264300 | 5190 | 1 | - Soft Cost | - Permitting and Engineering
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
133 | Repainting of walls and ceiling | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 875000 | 17160 | 1 | - walls are vandalized and stained | - Repainting of walls
134 | Supply and installation of linoleum flooring | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 225000 | 4420 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
134 | Supply and installation of linoleum flooring | Barracks - G2 | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 225000 | 4420 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 1860000 | 36480 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
135 | Replacement of Air-condition unit (Inverter type) | Barracks - G2 | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 62 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 1860000 | 36480 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
136 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - G2 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1500 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1500000 | 29420 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
137 | Miscellaneous Items | Barracks - G2 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 356800 | 0 | 1 | 0 |  |  | 0 | 356800 | 7000 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
138 | Contingencies (10%) | Barracks - G2 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 481700 | 0 | 1 | 0 |  | 0 | 0 | 481700 | 9450 | 1 | - Contingencies | 10% contingencies
139 | Preliminaries (10%) | Barracks - G2 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 529900 | 0 | 1 | 0 |  | 0 | 0 | 529900 | 10400 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
140 | Permitting and Engineering (5%) | Barracks - G2 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 291500 | 0 | 1 | 0 |  | 0 | 0 | 291500 | 5720 | 1 | - Soft Cost | - Permitting and Engineering
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
141 | Repainting of walls and ceiling | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 825000 | 16180 | 1 | - walls are vandalized and stained | - Repainting of walls
142 | Supply and installation of linoleum flooring | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 157500 | 3090 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
142 | Supply and installation of linoleum flooring | Barracks - D | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 157500 | 3090 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 5 | 2 | 1 | 5 | 1 | 45000 | 10 | 1 | 0 |  | 0 | 0 | 3780000 | 74120 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 10 |  | 0 | 0 | 3780000 | 74120 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
143 | Replacement of Air-condition unit (81 rooms + 3 Lounge) | Barracks - D | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 84 |  | no. | 0 | 1 | 1 | 8 | 1 | 45000 | 10 | 1 | 20 |  | 0 | 0 | 3780000 | 74120 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
144 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - D | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 |  | 1050000 | 20590 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
145 | Miscellaneous Items | Barracks - D | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 465000 | 0 | 1 | 0 |  |  |  | 465000 | 9120 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs - door knobs replacement - Replacement of broken windows - Replacement of sealants/waterproofing - Cleaning of confort rooms - Replacement of korean socket to 3-prong - Replacement of Fire Hose Cabinet
146 | Contingencies (10%) | Barracks - D | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 627800 | 0 | 1 | 0 |  | 0 | 0 | 627800 | 12310 | 1 | - Contingencies | 10% contingencies
147 | Preliminaries (10%) | Barracks - D | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 690600 | 0 | 1 | 0 |  | 0 | 0 | 690600 | 13550 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
148 | Permitting and Engineering (5%) | Barracks - D | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 379800 | 0 | 1 | 0 |  | 0 | 0 | 379800 | 7450 | 1 | - Soft Cost | - Permitting and Engineering
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 5 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
149 | Repainting of walls and ceiling | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 4050 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 |  | 1012500 | 19860 | 1 | - walls are vandalized and stained | - Repainting of walls
150 | Supply and installation of linoleum flooring | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 150 | 20 | 1 | 0 |  | 0 |  | 195000 | 3830 | 1 | - linoleum floor covers are in very poor condition and needs to be replaced | - Replacement of linoleum tiles
150 | Supply and installation of linoleum flooring | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 150 | 20 | 1 | 20 |  | 0 |  | 195000 | 3830 | 1 | - life expectancy of linoleum tiles | - Replacement of linoleum tiles
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 5 | 2 | 1 | 5 | 1 | 30000 | 10 | 1 | 0 |  | 0 | 0 | 3150000 | 61770 | 2 | - AC's have not been used after the shut down. - No maintenance was made for the AC - Already reached its end of life | - Replacement of AC to retain the room in as-built condition
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 10 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
151 | Replacement of Air-condition unit (Inverter type) | Barracks - E | 1 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 105 |  | no. | 0 | 1 | 1 | 8 | 1 | 30000 | 10 | 1 | 20 |  | 0 | 0 | 3150000 | 61770 | 2 | - life expectancy of AC | - Replacement of AC to retain the room in as-built condition
152 | Rehabilitation of Comfort Rooms and Shower Rooms | Barracks - E | 1 | NY | Navy | Interior | Architectural | Navy | 2006 | 200 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 400000 | 7850 | 1 | - all comfort rooms and shower rooms are in poor condition - Cracked slabs, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
153 | Electrical Works (extension of wirings, outlets including embedments) | Barracks - E | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1300 |  | m2 | 5 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 2 | -Most exposed electrical wires are in fair condition. - Some wires covers are delapidated (flaking) due to weather condition - Wires are still usable. however, in the long-run, this will impose safety concern. - If the capacity of the AC's will be changed from 0.75HP to 1HP, might consider replacing electrical wirings | - Replacement of Electrical wirings inlcuding providing insulations to protect wires from flaking
154 | Contingencies (10%) | Barracks - E | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 605800 | 0 | 1 | 0 |  | 0 | 0 | 605800 | 11880 | 1 | - Contingencies | 10% contingencies
155 | Preliminaries (10%) | Barracks - E | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 666400 | 0 | 1 | 0 |  | 0 | 0 | 666400 | 13070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
156 | Permitting and Engineering (5%) | Barracks - E | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 366500 | 0 | 1 | 0 |  | 0 | 0 | 366500 | 7190 | 1 | - Soft Cost | - Permitting and Engineering
157 | Overall Repair of the Facility | Convenience Store building | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 502 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 2 |  | 1 | 63100 | 2510000 | 49220 | 1 | - Cracks on Slab - Exhaust Fan Damage - Comfort Room stained and Filthy - House Cleaning - Damage Doors 2m x 2.1 m (1no) -Canopy Rusted - Korean brand socket - Repainting | Repair of this building will be dependend with the user. Assumed repaired within 2 years - Repairs of Slab - Replacement of Exhaust Fan - House cleaning - Replacement of Door 2mx2.1m (1no.) - Repainting of Canopy - Rehabilitation of comfor room - Replacement of Korean brand outlet to 3-prong universal socket - Repainting
158 | Contingencies (10%) | Convenience Store building | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 251000 | 0 | 1 | 2 |  | 0 | 0 | 251000 | 4930 | 1 | - Contingencies | 10% contingencies
159 | Preliminaries (10%) | Convenience Store building | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 276100 | 0 | 1 | 2 |  | 0 | 0 | 276100 | 5420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
160 | Permitting and Engineering (5%) | Convenience Store building | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 151900 | 0 | 1 | 2 |  | 0 | 0 | 151900 | 2980 | 1 | - Soft Cost | - Permitting and Engineering
161 | Overall Repair of the Facility | Canteen-Romanian | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 220 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 2 |  | 0 | 0 | 1100000 | 21570 | 1 | - Cracks on Slab - Exhaust Fan Damage - Comfort Room stained and Filthy - House Cleaning - Damage Doors 2m x 2.1 m (1no) -Canopy Rusted - Korean brand socket | - Repairs of Slab - Replacement of Exhaust Fan - House cleaning - Replacement of Door 2mx2.1m (1no.) - Repainting of Canopy - Rehabilitation of comfor room - Replacement of Korean brand outlet to 3-prong universal socket
162 | Contingencies (10%) | Canteen-Romanian | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110000 | 0 | 1 | 2 |  | 0 | 0 | 110000 | 2160 | 1 | - Contingencies | 10% contingencies
163 | Preliminaries (10%) | Canteen-Romanian | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121000 | 0 | 1 | 2 |  | 0 | 0 | 121000 | 2380 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
164 | Permitting and Engineering (5%) | Canteen-Romanian | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66600 | 0 | 1 | 2 |  | 0 | 0 | 66600 | 1310 | 1 | - Soft Cost | - Permitting and Engineering
165 | Overall Repair of the Facility | Air Compressed Room - 2,3 | 1 | NY | Austal | Miscellaneous | Miscellaneous | Austal | 2016 | 382 |  | m2 | 2 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.4 | 0 |  | 1 | 87700 | 764000 | 14990 | 1 | - Missing Cross Rod Brace - Damage Roller-up door | - Replacement of Cross Rod Brace - Replacement of Roller-up Door 5m x9m (1no)
166 | Panel Boards | Air Compressed Room - 2,3 | 1 | NY | Austal | Electrical System | Electrical | Austal | 2016 | 1 |  | lot | 2 | 1 | 1 | 5 | 1 | 2559690 | 25 | 1 | 21 |  | 1 | 50190 | 2559690 | 50190 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
167 | Upgrade to comply current structural code | Air Compressed Room - 2,3 | 1 | NY | Austal | Structural Upgrade | Structural | Austal | 2016 | 382 |  | lot | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - No CapEx will be included in Phase 2
168 | Contingencies (10%) | Air Compressed Room - 2,3 | lot | NY | Austal | Contingencies | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76400 | 0 | 1 | 0 |  | 0 | 0 | 76400 | 1500 | 1 | - Contingencies | 10% contingencies
169 | Preliminaries (10%) | Air Compressed Room - 2,3 | lot | NY | Austal | Preliminaries | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84100 | 0 | 1 | 0 |  | 0 | 0 | 84100 | 1650 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
170 | Permitting and Engineering (5%) | Air Compressed Room - 2,3 | lot | NY | Austal | Engineering and Management | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46300 | 0 | 1 | 0 |  | 0 | 0 | 46300 | 910 | 1 | - Soft Cost | - Permitting and Engineering
171 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
172 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 15 | 1 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting to be moved to its life expectancy
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
173 | Repainting of Walls 2nd Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
174 | Repainting of Walls 1st Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 3 | 2 | 1 | 8 | 1 | 250 | 10 | 1 | 6 |  | 0 | 0 | 315000 | 6180 | 1 | - Wall paint in this floor still in fair condition. - From life expectancy, wall paint has only 2 years left | - Repainting of wall due to life expectancy
174 | Repainting of Walls 1st Floor | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 16 |  | 0 |  | 315000 | 6180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
175 | Replacement of Ceiling Boards | Field Office 15 | 2 | NY | Austal | Interior | Architectural | Austal | 2016 | 400 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 11 |  | 0 | 0 | 240000 | 4710 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
176 | Replacement of DX type units | Field Office 15 | 2 | NY | Austal | HVAC | Mechanical | Austal | 2016 | 20 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 2760000 | 54120 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
176 | Replacement of DX type units | Field Office 15 | 2 | NY | Austal | HVAC | Mechanical | Austal | 2016 | 20 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 2760000 | 54120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
177 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 15 | Lot | NY | Austal | Electrical System | Electrical | Austal | 2016 | 400 |  | m2 | 4 | 3 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
177 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 15 | Lot | NY | Austal | Electrical System | Electrical | Austal | 2016 | 400 |  | m2 | 1 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
178 | Repair of roofs and gutters | Field Office 15 | Lot | NY | Austal | Roof | Roof | Austal | 2016 | 430 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
179 | Miscellaneous Items | Field Office 15 | 1 | NY | Austal | Miscellaneous | Miscellaneous | Austal | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 460000 | 0 | 1 | 0 |  |  |  | 460000 | 9020 | 1 | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs | - Allocation for the unforeseen repair/installation such as fire extinguishers, signages - house cleaning - minor repairs
180 | Contingencies (10%) | Field Office 15 | lot | NY | Austal | Contingencies | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 506000 | 0 | 1 | 0 |  | 0 | 0 | 506000 | 9930 | 1 | - Contingencies | 10% contingencies
181 | Preliminaries (10%) | Field Office 15 | lot | NY | Austal | Preliminaries | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 556600 | 0 | 1 | 0 |  | 0 | 0 | 556600 | 10920 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
182 | Permitting and Engineering (5%) | Field Office 15 | lot | NY | Austal | Engineering and Management | Soft Cost | Austal | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 300200 | 0 | 1 | 0 |  | 0 | 0 | 300200 | 5890 | 1 | - Soft Cost | - Permitting and Engineering
183 | Overall Repair of the Facility | Main Gate | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1342 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.3 | 2 |  | 0 | 0 | 2013000 | 39480 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
184 | Upgrade to comply current structural code | Main Gate | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 1342 |  | m2 | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 39470 | 1610400 | 31580 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
185 | Contingencies (10%) | Main Gate | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 362400 | 0 | 1 | 0 |  | 0 | 0 | 362400 | 7110 | 1 | - Contingencies | 10% contingencies
186 | Preliminaries (10%) | Main Gate | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 398600 | 0 | 1 | 0 |  | 0 | 0 | 398600 | 7820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
187 | Permitting and Engineering (5%) | Main Gate | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 219300 | 0 | 1 | 0 |  | 0 | 0 | 219300 | 4300 | 1 | - Soft Cost | - Permitting and Engineering
188 | Overall Repair of the Facility | Shelter 712 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.3 | 0 |  | 0 | 0 | 1650000 | 32360 | 1 | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element
189 | Replacement of polycarbornate Roof | Shelter 712 | 1 | NY | Navy | Roof | Roof | Navy | 2006 | 160 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 1 | 12700 | 320000 | 6280 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
190 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Shelter 712 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 0 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
191 | Contingencies (10%) | Shelter 712 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Contingencies | 10% contingencies
192 | Preliminaries (10%) | Shelter 712 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 181500 | 0 | 1 | 0 |  | 0 | 0 | 181500 | 3560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
193 | Permitting and Engineering (5%) | Shelter 712 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 99900 | 0 | 1 | 0 |  | 0 | 0 | 99900 | 1960 | 1 | - Soft Cost | - Permitting and Engineering
194 | Provision for the storm drainage | Assembly Shop (D) | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2016 | 800 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 4000000 | 78440 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
195 | Upgrade to comply current structural code | Assembly Shop (D) | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2016 | 11880 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 342700 | 2376000 | 46590 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
196 | Replacement of polycarbornate Roof | Assembly Shop (D) | 1 | NY | Navy | Roof | Roof | Navy | 2016 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 1 | 57120 | 6600000 | 129420 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
197 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Assembly Shop (D) | 1 | NY | Navy | Electrical System | Electrical | Navy | 2016 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 21 |  | 0 | 16030 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
198 | Miscellaneous Items | Assembly Shop (D) | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 318800 | 0 | 1 | 0 |  | 0 | 0 | 318800 | 6260 | 1 | - Repainting of rusted steel frame members | - Repainting of rusted steel frame members
199 | Contingencies (10%) | Assembly Shop (D) | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 669500 | 0 | 1 | 0 |  | 0 | 0 | 669500 | 13130 | 1 | - Contingencies | 10% contingencies
200 | Preliminaries (10%) | Assembly Shop (D) | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 736500 | 0 | 1 | 0 |  | 0 | 0 | 736500 | 14450 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
201 | Permitting and Engineering (5%) | Assembly Shop (D) | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 405100 | 0 | 1 | 0 |  | 0 | 0 | 405100 | 7950 | 1 | - Soft Cost | - Permitting and Engineering
202 | Provision for the storm drainage | Blasting & Painting Shop E | 1 | NY | Navy | Plumbing System | Plumbing | Navy | 2016 | 250 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1250000 | 24510 | 2 | - Damage Downspout - No proper drainage of downspout | - Damage Downspout - No proper drainage of downspout - Repair of buckled structural steel element
203 | Upgrade to comply current structural code | Blasting & Painting Shop E | 1 | NY | Navy | Structural Upgrade | All Disciplines | Navy | 2016 | 5913 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 170570 | 1182600 | 23190 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
204 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop E | 1 | NY | Navy | Roof | Roof | Navy | 2016 | 3300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 0 | 6 |  | 1 | 284280 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
205 | Miscellaneous Items | Blasting & Painting Shop E | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 243300 | 0 | 1 | 0 |  | 0 | 0 | 243300 | 4780 | 1 | - Repainting of rusted steel frame members | - Repainting of rusted steel frame members
206 | Contingencies (10%) | Blasting & Painting Shop E | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 267600 | 0 | 1 | 0 |  | 0 | 0 | 267600 | 5250 | 1 | - Contingencies | 10% contingencies
207 | Preliminaries (10%) | Blasting & Painting Shop E | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 294400 | 0 | 1 | 0 |  | 0 | 0 | 294400 | 5780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
208 | Permitting and Engineering (5%) | Blasting & Painting Shop E | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 161900 | 0 | 1 | 0 |  | 0 | 0 | 161900 | 3180 | 1 | - Soft Cost | - Permitting and Engineering
209 | Provision for the storm drainage | Field Office 2A | Lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
210 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 216000 | 4240 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
211 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 216000 | 4240 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 30500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
212 | Repainting of Walls 2nd Floor | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
213 | Repainting of Walls 1st Floor | Field Office 2A | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
214 | Replacement of Ceiling Boards | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 432000 | 8480 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
214 | Replacement of Ceiling Boards | Field Office 2A | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 432000 | 8480 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2484000 | 48710 | 1 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
215 | Replacement of DX type units | Field Office 2A | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4968000 | 97420 | 1 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
216 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 2A | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 720000 | 14120 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
217 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 2A | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1440000 | 28240 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
218 | Repair of roofs and gutters | Field Office 2A | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 8500 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
219 | Miscellaneous items | Field Office 2A | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1152600 | 0 | 1 | 0 |  | 0 | 0 | 1152600 | 22600 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
220 | Contingencies (10%) | Field Office 2A | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1267900 | 0 | 1 | 0 |  | 0 | 0 | 1267900 | 24870 | 1 | - Contingencies | 10% contingencies
221 | Preliminaries (10%) | Field Office 2A | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1394700 | 0 | 1 | 0 |  | 0 | 0 | 1394700 | 27350 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
222 | Permitting and Engineering (5%) | Field Office 2A | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 767100 | 0 | 1 | 0 |  | 0 | 0 | 767100 | 15050 | 1 | - Soft Cost | - Permitting and Engineering
223 | Provision for the storm drainage | Field Office 2 | Lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 150 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
224 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 640 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 192000 | 3770 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
225 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 640 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 192000 | 3770 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 510 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 27000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 510 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 127500 | 2500 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
226 | Repainting of Walls 2nd Floor | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
227 | Repainting of Walls 1st Floor | Field Office 2 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 600 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 150000 | 2950 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
228 | Replacement of Ceiling Boards | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 432000 | 8480 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
228 | Replacement of Ceiling Boards | Field Office 2 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 720 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 432000 | 8480 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2484000 | 48710 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
229 | Replacement of DX type units | Field Office 2 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 36 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4968000 | 97420 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
230 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 2 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 720000 | 14120 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
231 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 2 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 720 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1440000 | 28240 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
232 | Repair of roofs and gutters | Field Office 2 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 720 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
233 | Miscellaneous items | Field Office 2 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1145600 | 0 | 1 | 0 |  | 0 | 0 | 1145600 | 22470 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
234 | Contingencies (10%) | Field Office 2 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1260200 | 0 | 1 | 0 |  | 0 | 0 | 1260200 | 24710 | 1 | - Contingencies | 10% contingencies
235 | Preliminaries (10%) | Field Office 2 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1386200 | 0 | 1 | 0 |  | 0 | 0 | 1386200 | 27190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
236 | Permitting and Engineering (5%) | Field Office 2 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 762400 | 0 | 1 | 0 |  | 0 | 0 | 762400 | 14950 | 1 | - Soft Cost | - Permitting and Engineering
237 | Upgrade to comply current structural code | No.5 Dock Shelter | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 4950 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 136300 | 4950000 | 97060 | 2 | ` | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
238 | Replacement of Angle Cross Brace | No.5 Dock Shelter | 1 | SY | Austal | Structural Elements | Structural | Austal | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 1856400 | 0 | 0 | 0 |  | 1 | 36400 | 0 | 0 | 0 | - During our latest site inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
239 | Overall Repair of the facility | No.5 Dock Shelter | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 4950 |  | m2 | 3 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 2475000 | 48530 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of roof with holes | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of roof with holes
240 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | No.5 Dock Shelter | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 49840 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
241 | Replacement of polycarbornate Roof and Wall | No.5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 320 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 640000 | 12550 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
242 | Contingencies (10%) | No.5 Dock Shelter | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 742500 | 0 | 1 | 0 |  | 0 | 0 | 742500 | 14560 | 1 | - Contingencies | 10% contingencies
243 | Preliminaries (10%) | No.5 Dock Shelter | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 816800 | 0 | 1 | 0 |  | 0 | 0 | 816800 | 16020 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
244 | Permitting and Engineering (5%) | No.5 Dock Shelter | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 449300 | 0 | 1 | 0 |  | 0 | 0 | 449300 | 8810 | 1 | - Soft Cost | - Permitting and Engineering
245 | Upgrade to comply current structural code | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 17220 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 147120 | 17220000 | 337650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
246 | Repair of GI Roof and Wall | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 750 |  | m2 | 5 | 3 | 1 | 5 | 1 | 2500 | 50 | 1 | 0 |  | 1 | 114500 | 1875000 | 36770 | 1 | - observed that section of roofs has some holes | - repair of roofs
247 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 0 | 13790 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
248 | Overall Repair of the facility | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 17220 |  | m2 | 3 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.05 | 0 |  | 1 | 87700 | 4305000 | 84420 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of rusted GI sheet wall | - Repainting of rusted steel frame members -Repair of buckled steel frame - Supply and install of drainage steel grating - Replacement of rusted GI sheet wall
249 | Replacement of polycarbornate Roof and Wall | Pre-erection area (6 nos) - No. 5 Dock Shelter | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 320 |  | m2 | 3 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 640000 | 12550 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
250 | Contingencies (10%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2340000 | 0 | 1 | 0 |  | 0 | 0 | 2340000 | 45890 | 1 | - Contingencies | 10% contingencies
251 | Preliminaries (10%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2574000 | 0 | 1 | 0 |  | 0 | 0 | 2574000 | 50480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
252 | Permitting and Engineering (5%) | Pre-erection area (6 nos) - No. 5 Dock Shelter | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1415700 | 0 | 1 | 0 |  | 0 | 0 | 1415700 | 27760 | 1 | - Soft Cost | - Permitting and Engineering
253 | Upgrade to comply current structural code | Hatch cover Shelter | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2006 | 16000 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 912700 | 19200000 | 376480 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
254 | Repair of Roof Frames | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 116400 |  | kg | 5 | 1 | 1 | 5 | 0.2 | 200 | 0 | 1 | 0 |  | 1 | 22600 | 4656000 | 91300 | 1 | - Replacement of angle cross brace included in the Overall repair of the facility | - Replacement of angle cross brace included in the Overall repair of the facility
255 | Gas port/ Electrical Panel Location Provision of Barricade | Hatch cover Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 2632500 | 25 | 0 | 2 |  | 1 | 744500 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
255 | Gas port/ Electrical Panel Location Provision of Barricade | Hatch cover Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 2632500 | 25 | 1 | 0 |  | 1 |  | 2632500 | 51620 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
256 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Hatch cover Shelter | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 49840 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
257 | Replacement of polycarbornate Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 1716 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 343200 | 6730 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
257 | Replacement of polycarbornate Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 1716 |  | m2 | 1 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 3432000 | 67300 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
258 | Repair of GI Roof and Wall | Hatch cover Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 25200 |  | m2 | 5 | 1 | 1 | 2 | 0.05 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 3150000 | 61770 | 1 | - observed that section of roofs has some holes | - repair of roofs
259 | Miscellaneous Items | Hatch cover Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1499100 | 0 | 1 | 0 |  | 0 | 0 | 1499100 | 29400 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal
260 | Contingencies (10%) | Hatch cover Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3148100 | 0 | 1 | 0 |  | 0 | 0 | 3148100 | 61730 | 1 | - Contingencies | 10% contingencies
261 | Preliminaries (10%) | Hatch cover Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3462900 | 0 | 1 | 0 |  | 0 | 0 | 3462900 | 67900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
262 | Permitting and Engineering (5%) | Hatch cover Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1904600 | 0 | 1 | 0 |  | 0 | 0 | 1904600 | 37350 | 1 | - Soft Cost | - Permitting and Engineering
263 | Upgrade to comply current structural code | Dhouse Shelter | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2006 | 15180 |  | m2 | 3 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 452890 | 15180000 | 297650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
264 | Replacement of Angle Cross Brace | Dhouse Shelter | 1 | NY | Tenant 3 | Structural Elements | Structural | Tenant 3 | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 0 | 0 | 0 | 0 |  | 1 | 19300 | 0 | 0 | 0 | - During our latest site inspection, we did not found any structural defects/deformation on any of the steel members | - No Capex will be allocated to Phase 2
265 | Gas port/ Electrical Panel Location Provision of Barricade | Dhouse Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 3276000 | 25 | 0 | 2 |  | 1 | 638200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
265 | Gas port/ Electrical Panel Location Provision of Barricade | Dhouse Shelter | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2006 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 3276000 | 25 | 1 | 0 |  | 1 |  | 3276000 | 64240 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
266 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Dhouse Shelter | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 36540 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
267 | Replacement of polycarbornate Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 2160 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
267 | Replacement of polycarbornate Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 2160 |  | m2 | 0 | 1 | 1 | 8 | 1 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 4320000 | 84710 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
268 | Repair of GI Roof and Wall | Dhouse Shelter | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2006 | 24400 |  | m2 | 5 | 1 | 1 | 2 | 0.05 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 3050000 | 59810 | 1 | - observed that section of roofs has some holes | - repair of roofs
269 | Miscellaneous Items | Dhouse Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2237000 | 0 | 1 | 0 |  | 0 | 0 | 2237000 | 43870 | 1 | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal | - Repainting of rusted steel frame members -Repair of buckled steel frame - Replacement of roof with holes - Hauling and Disposal
270 | Contingencies (10%) | Dhouse Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2460700 | 0 | 1 | 0 |  | 0 | 0 | 2460700 | 48250 | 1 | - Contingencies | 10% contingencies
271 | Preliminaries (10%) | Dhouse Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2706800 | 0 | 1 | 0 |  | 0 | 0 | 2706800 | 53080 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
272 | Permitting and Engineering (5%) | Dhouse Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1488800 | 0 | 1 | 0 |  | 0 | 0 | 1488800 | 29200 | 1 | - Soft Cost | - Permitting and Engineering
273 | Upgrade to comply current structural code | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2016 | 10800 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.05 | 0 |  | 1 | 311540 | 2160000 | 42360 | 2 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - may not require retrofitting
274 | Gas port/ Electrical Panel Location Provision of Barricade | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2016 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 1768000 | 25 | 0 | 2 |  | 1 | 254200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gas port and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
274 | Gas port/ Electrical Panel Location Provision of Barricade | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2016 | 1 |  | lot | 5 | 3 | 1 | 5 | 1 | 1768000 | 25 | 1 | 0 |  | 1 |  | 1768000 | 34670 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gas port and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
275 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2016 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 11 |  | 1 | 14560 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
276 | Replacement of polycarbornate Roof and Wall | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2016 | 10800 |  | m2 | 3 | 1 | 1 | 5 | 0.05 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
276 | Replacement of polycarbornate Roof and Wall | Sub-Assembly Shop (94 bay) | 1 | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2016 | 10800 |  | m2 | 1 | 1 | 1 | 8 | 0.5 | 2000 | 25 | 1 | 16 |  | 0 | 0 | 10800000 | 211770 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
277 | Provision for the storm drainage | Sub-Assembly Shop (94 bay) | Lot | SY | Tenant 3 | Plumbing System | Plumbing | Tenant 3 | 2016 | 450 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 2250000 | 44120 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
278 | Miscellaneous Items | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1088700 | 0 | 1 | 0 |  | 0 | 0 | 1088700 | 21350 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - connecting of downspout to the nearest drainage - cleaning and hauling - rusted members for repainting - peeled off paints
279 | Contingencies (10%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 834700 | 0 | 1 | 0 |  | 0 | 0 | 834700 | 16370 | 1 | - Contingencies | 10% contingencies
280 | Preliminaries (10%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 918200 | 0 | 1 | 0 |  | 0 | 0 | 918200 | 18010 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
281 | Permitting and Engineering (5%) | Sub-Assembly Shop (94 bay) | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 505000 | 0 | 1 | 0 |  | 0 | 0 | 505000 | 9910 | 1 | - Soft Cost | - Permitting and Engineering
282 | Upgrade to comply current structural code | Outfitting Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 5600 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.3 | 0 |  | 0 | 0 | 6720000 | 131770 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
283 | Replacement of polycarbornate Roof and Wall | Outfitting Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5600 |  | m2 | 3 | 1 | 1 | 5 | 0.05 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 560000 | 10990 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
283 | Replacement of polycarbornate Roof and Wall | Outfitting Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5600 |  | m2 | 1 | 1 | 1 | 8 | 0.5 | 2000 | 25 | 1 | 6 |  | 0 | 0 | 5600000 | 109810 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
284 | Miscellaneous Items | Outfitting Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1456000 | 0 | 1 | 0 |  | 0 | 0 | 1456000 | 28550 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - fastening of steel storage racks | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - fastening of steel storage racks
285 | Contingencies (10%) | Outfitting Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 873600 | 0 | 1 | 0 |  | 0 | 0 | 873600 | 17130 | 1 | - Contingencies | 10% contingencies
286 | Preliminaries (10%) | Outfitting Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 961000 | 0 | 1 | 0 |  | 0 | 0 | 961000 | 18850 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
287 | Permitting and Engineering (5%) | Outfitting Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 528600 | 0 | 1 | 0 |  | 0 | 0 | 528600 | 10370 | 1 | - Soft Cost | - Permitting and Engineering
288 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 178200 | 3500 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
289 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 178200 | 3500 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 25400 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
290 | Repainting of Walls 2nd Floor | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
291 | Repainting of Walls 1st Floor | Field Office 5A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
292 | Replacement of Ceiling Boards | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 356400 | 6990 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
292 | Replacement of Ceiling Boards | Field Office 5A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 594 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 356400 | 6990 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 3 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4140000 | 81180 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4140000 | 81180 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
293 | Replacement of DX type units | Field Office 5A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 30 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4140000 | 81180 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
294 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 5A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 594000 | 11650 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
295 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 5A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 594 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1188000 | 23300 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
296 | Repair of roofs and gutters | Field Office 5A | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 594 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7100 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
297 | Miscellaneous items | Field Office 5A | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 687500 | 0 | 1 | 0 |  | 0 | 0 | 687500 | 13490 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms
298 | Contingencies (10%) | Field Office 5A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 756300 | 0 | 1 | 0 |  | 0 | 0 | 756300 | 14830 | 1 | - Contingencies | 10% contingencies
299 | Preliminaries (10%) | Field Office 5A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 831900 | 0 | 1 | 0 |  | 0 | 0 | 831900 | 16320 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
300 | Permitting and Engineering (5%) | Field Office 5A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 457600 | 0 | 1 | 0 |  | 0 | 0 | 457600 | 8980 | 1 | - Soft Cost | - Permitting and Engineering
301 | Repair of Structural Steel frame members | Electric Steel Outfitting Shop | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 99000 |  | kg | 4 | 3 | 1 | 5 | 0.2 | 200 | 0 | 1 | 0 |  | 1 | 88300 | 3960000 | 77650 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
302 | Upgrade to comply current structural code | Electric Steel Outfitting Shop | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 3300 |  | m2 | 4 | 3 | 0 | 5 | 1 | 4000 | 0 | 0.7 | 0 |  | 1 | 252730 | 9240000 | 181180 | 2 | -The building was constructed in 2012 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
303 | Replacement of polycarbornate Roof and Wall | Electric Steel Outfitting Shop | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 400 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 17 |  | 0 | 0 | 800000 | 15690 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
304 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Electric Steel Outfitting Shop | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 17 |  | 1 | 2730 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
305 | Miscellaneous Items | Electric Steel Outfitting Shop | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2640000 | 0 | 1 | 0 |  | 0 | 0 | 2640000 | 51770 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
306 | Contingencies (10%) | Electric Steel Outfitting Shop | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1584000 | 0 | 1 | 0 |  | 0 | 0 | 1584000 | 31060 | 1 | - Contingencies | 10% contingencies
307 | Preliminaries (10%) | Electric Steel Outfitting Shop | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1742400 | 0 | 1 | 0 |  | 0 | 0 | 1742400 | 34170 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
308 | Permitting and Engineering (5%) | Electric Steel Outfitting Shop | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 958400 | 0 | 1 | 0 |  | 0 | 0 | 958400 | 18800 | 1 | - Soft Cost | - Permitting and Engineering
309 | Overall Repair of the facility | Electric Steel Outfitting Shop (Building at the back) | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1000 |  | m2 | 5 | 3 | 1 | 5 | 1 | 5000 | 0 | 1 | 0 |  | 1 | 230500 | 5000000 | 98040 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
310 | Replacement of GI wall sheet | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 360 |  | m2 | 4 | 3 | 1 | 5 | 1 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 900000 | 17650 | 1 | - Roofs are damaged | - replacement of GI sheet roof
311 | Replacement of polycarbornate Roof | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 750 | 25 | 1 | 0 |  | 0 | 0 | 75000 | 1480 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
311 | Replacement of polycarbornate Roof | Electric Steel Outfitting Shop (Building at the back) | 1 | SY | Navy | Roof | Roof | Navy | 2012 | 1000 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 750 | 25 | 1 | 25 |  | 0 | 0 | 75000 | 1480 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
312 | Miscellaneous Items | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1195000 | 0 | 1 | 0 |  | 0 | 0 | 1195000 | 23440 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
313 | Contingencies (10%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 717000 | 0 | 1 | 0 |  | 0 | 0 | 717000 | 14060 | 1 | - Contingencies | 10% contingencies
314 | Preliminaries (10%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 788700 | 0 | 1 | 0 |  | 0 | 0 | 788700 | 15470 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
315 | Permitting and Engineering (5%) | Electric Steel Outfitting Shop (Building at the back) | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 433800 | 0 | 1 | 0 |  | 0 | 0 | 433800 | 8510 | 1 | - Soft Cost | - Permitting and Engineering
316 | Repair of C-purlins for GI Sheet Wall | Cable Cutting | 1 | NY | Navy | Structural Elements | Structural | Navy | 2012 | 13600 |  | kg | 4 | 2 | 1 | 5 | 1 | 200 | 50 | 1 | 0 |  | 0 | 0 | 2720000 | 53340 | 1 | Observed deformation of structural members | Repair of deformed / buckled stell frame members
317 | Replacement of polycarbornate Roof and Wall | Cable Cutting | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 2040 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1224000 | 24000 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
317 | Replacement of polycarbornate Roof and Wall | Cable Cutting | 1 | NY | Navy | Roof | Roof | Navy | 2012 | 2040 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 1 | 17 |  | 0 | 0 | 4080000 | 80000 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
318 | Upgrade to comply current structural code | Cable Cutting | 1 | NY | Navy | Structural Upgrade | Structural | Navy | 2012 | 1250 |  | m2 | 4 | 2 | 0 | 4 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 0 | 1250000 | 24510 | 2 | -The building was constructed in 2012 and is assumed that the code used was NSCP 2010. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
319 | Power Distribution Local Panel (Consolidation Outlet)(440V&220V) | Cable Cutting | 1 | NY | Navy | Electrical System | Electrical | Navy | 2012 | 102 |  | sets | 3 | 1 | 1 | 8 | 1 | 35000 | 25 | 1 | 17 |  | 1 | 2730 | 3570000 | 70000 | 1 | - Power Distribution Local Panel including circuit breakers and switches are to be replaced in 25 years due to itS end of service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement Power Distribution Local Panel due to its end of life service
320 | Miscellaneous Items | Cable Cutting | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2012 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1038800 | 0 | 1 | 0 |  | 0 | 0 | 1038800 | 20370 | 1 | - Deteriorated wall cladding - Missing and damaged window grills and cover - Damage circular steel beam - Cleaning and hauling - Rusted structural members - Visible cracks on slab | - Replacement of wall cladding - Repair of window grills and cover - Repair damage in circular steel beam - Cleaning and hauling - Repainting of structure - Application of concrete epoxy
321 | Contingencies (10%) | Cable Cutting | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 623300 | 0 | 1 | 0 |  | 0 | 0 | 623300 | 12230 | 1 | - Contingencies | 10% contingencies
322 | Preliminaries (10%) | Cable Cutting | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 685700 | 0 | 1 | 0 |  | 0 | 0 | 685700 | 13450 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
323 | Permitting and Engineering (5%) | Cable Cutting | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2012 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 377100 | 0 | 1 | 0 |  | 0 | 0 | 377100 | 7400 | 1 | - Soft Cost | - Permitting and Engineering
324 | Overall Repair of the Facility | Gasoline Station | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 300 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
325 | Contingencies (10%) | Gasoline Station | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Contingencies | 10% contingencies
326 | Preliminaries (10%) | Gasoline Station | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
327 | Permitting and Engineering (5%) | Gasoline Station | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Soft Cost | - Permitting and Engineering
328 | Overall Repair of the Facility | Helicopter Hangar | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 900 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 2250000 | 44120 | 1 | - Damage Rain gutter - Vinyl tile dilapidated - Korean socket - Repainting | - Damage Rain gutter - Vinyl tile dilapidated - Korean socket - Repainting
329 | Contingencies (10%) | Helicopter Hangar | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 225000 | 0 | 1 | 0 |  | 0 | 0 | 225000 | 4420 | 1 | - Contingencies | 10% contingencies
330 | Preliminaries (10%) | Helicopter Hangar | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 247500 | 0 | 1 | 0 |  | 0 | 0 | 247500 | 4860 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
331 | Permitting and Engineering (5%) | Helicopter Hangar | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 136200 | 0 | 1 | 0 |  | 0 | 0 | 136200 | 2680 | 1 | - Soft Cost | - Permitting and Engineering
332 | Upgrade to comply current structural code | Main Office | Lot | NY | Navy | Structural Upgrade | Structural | Navy | 2006 | 14000 |  | m2 | 5 | 2 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 0 | 14000000 | 274510 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
333 | Removal and Replacement of Carpets | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 15000 |  | m2 | 3 | 2 | 1 | 5 | 0.7 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 10500000 | 205890 | 4 | - Carpets are worn-out, stained, filty and dirty | - Removal and Installation of carpets,
334 | Replacement of Ceiling Boards | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 15000 |  | m2 | 3 | 2 | 1 | 5 | 0.5 | 600 | 0 | 1 | 0 |  | 1 | 37300 | 4500000 | 88240 | 1 | - Some ceiling boards are either sagging, stained damaged | - Replacement of ceiling boards to as-built condition
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 98300 | 2250000 | 44120 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 2250000 | 44120 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
335 | Repainting of Walls | Main Office | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 9000 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 2250000 | 44120 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
336 | Electrical Works (Installation and replacement of defective wirings, replacements of outlets including embedments) | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 15000 |  | m2 | 5 | 3 | 1 | 4 | 1 | 750 | 0 | 1 | 0 |  | 0 | 0 | 11250000 | 220590 | 1 | - All wires are messed and are scattered around the places which is a safety concern of tripping - Outlets are in korean brand | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition - Replacement of outlets to Philippines standard
337 | Electrical & Auxillary Equipments | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 15000 |  | m2 | 3 | 1 | 1 | 8 | 1 | 1000 | 30 | 1 | 16 |  | 0 | 0 | 15000000 | 294120 | 1 | -End of Life | -Replacement of All Panelboards, CCTV Equipments, PA/BGM Equipments, FDAS Equipments due to 30 yrs life span
338 | Removal and installation of waterproofing | Main Office | Roof | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1500 | 25 | 1 | 0 |  | 1 | 53900 | 5250000 | 102950 | 1 | - Machine room including the presidents room has stained water leaks on the ceiling | - Reinstallation of waterproofing
338 | Removal and installation of waterproofing | Main Office | Roof | NY | Navy | Interior | Architectural | Navy | 2006 | 3500 |  | m2 | 0 | 1 | 1 | 8 | 1 | 1500 | 25 | 1 | 11 |  | 0 | 0 | 5250000 | 102950 | 1 | - life expectancy of water proofing | - Reinstallation of waterproofing
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 10 | 1 | 5 |  | 1 | 1952000 | 8000000 | 156870 | 2 | - one chiller system has a serious gushing of water and needs to be replace immediately - Current alternative solution is feasible; however, efficiency | - replacement of HVAC system
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 3 |  | lot | 0 | 1 | 1 | 8 | 0.2 | 8000000 | 30 | 1 | 5 |  | 0 | 0 | 4800000 | 94120 | 2 | - '- HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be use as gushing already provided alternative repair solution; however, efficiency cannot be maximize due to its condition. | - replacement of refrigerant and compressor to comply with the phase-out of the R22
339 | HVAC System | Main Office | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 2 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 30 | 1 | 16 |  | 0 | 0 | 16000000 | 313730 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
340 | Lifts | Main Office | Lot | NY | Navy | Vertical Transportation | Mechanical | Navy | 2006 | 1 |  | lot | 4 | 1 | 1 | 2 | 0.3 | 1500000 | 25 | 1 | 0 |  | 1 | 11800 | 450000 | 8830 | 1 | - Elevators does not comply with the overweight capacity | - testing of elevator
340 | Lifts | Main Office | Lot | NY | Navy | Vertical Transportation | Mechanical | Navy | 2006 | 3 |  | no. | 1 | 1 | 1 | 8 | 1 | 1500000 | 25 | 1 | 11 |  | 1 | 0 | 4500000 | 88240 | 1 | - Elevators does not comply with the overweight capacity | - testing of elevator
341 | Provision for the storm drainage | Main Office | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2006 | 350 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 164800 | 1750000 | 34320 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
342 | Panel Boards | Main Office | lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 642600 | 25 | 1 | 11 |  | 0 | 12600 | 642600 | 12600 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
343 | Miscellaneous items | Main Office | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 3137500 | 0 | 1 | 0 |  | 1 | 89800 | 3137500 | 61520 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms - Cleaning of exterior facade - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - Hauling and Disposal of unused appliances and furnitures - supply and installation of ceiling fan - House Cleaning - Restoration of Comfort rooms - Cleaning of exterior facade - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities
344 | Miscellaneous items 2 | Main Office | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1462500 | 0 | 1 | 3 |  | 1 | 11600 | 1462500 | 28680 | 1 | - Allocation for the unforeseen repair/installation such as - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities | - Allocation for the unforeseen repair/installation such as - Reinstallation of window sealants - Replacement of damage water closet and other comfort room utilities
345 | Contingencies (10%) | Main Office | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6735000 | 0 | 1 | 0 |  | 0 | 0 | 6735000 | 132060 | 1 | - Contingencies | 10% contingencies
346 | Preliminaries (10%) | Main Office | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 7408500 | 0 | 1 | 0 |  | 0 | 0 | 7408500 | 145270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
347 | Permitting and Engineering (5%) | Main Office | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4074700 | 0 | 1 | 0 |  | 0 | 0 | 4074700 | 79900 | 1 | - Soft Cost | - Permitting and Engineering
348 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
349 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 97500 | 1920 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
350 | Repainting of Walls 2nd Floor | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 97500 | 1920 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
351 | Repainting of Walls 1st Floor | Field Office 5 | 1 | SY | Navy | Interior | Architectural | Navy | 2006 | 390 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 97500 | 1920 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
352 | Replacement of Ceiling Boards | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 259200 | 5090 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
352 | Replacement of Ceiling Boards | Field Office 5 | 2 | NY | Navy | Interior | Architectural | Navy | 2006 | 432 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 259200 | 5090 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3036000 | 59530 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
353 | Replacement of DX type units | Field Office 5 | 2 | NY | Navy | HVAC | Mechanical | Navy | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
354 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 5 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 432000 | 8480 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
355 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 5 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
356 | Repair of roofs and gutters | Field Office 5 | Lot | NY | Navy | Roof | Roof | Navy | 2006 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
357 | Miscellaneous items | Field Office 5 | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 403632 | 0 | 1 | 0 |  | 0 | 0 | 403632 | 7920 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
358 | Contingencies (10%) | Field Office 5 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 545000 | 0 | 1 | 0 |  | 0 | 0 | 545000 | 10690 | 1 | - Contingencies | 10% contingencies
359 | Preliminaries (10%) | Field Office 5 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 599500 | 0 | 1 | 0 |  | 0 | 0 | 599500 | 11760 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
360 | Permitting and Engineering (5%) | Field Office 5 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 329700 | 0 | 1 | 0 |  | 0 | 0 | 329700 | 6470 | 1 | - Soft Cost | - Permitting and Engineering
361 | Overall Repair of the Facility | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 3950 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 9875000 | 193630 | 1 | - Broken Controls of motorized sliding doors - dilapidated Rubber gasket of motorized sliding door - Steel storage rack not fixed - Container offices for rehabilitation | - Repair of controls of motorized sliding doors - Replacement of rubber gasket of motorized doors - installation of bolts of the storage steel racks - rehabilitation of contatiner offices
362 | Contingencies (10%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 987500 | 0 | 1 | 0 |  | 0 | 0 | 987500 | 19370 | 1 | - Contingencies | 10% contingencies
363 | Preliminaries (10%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1086300 | 0 | 1 | 0 |  | 0 | 0 | 1086300 | 21300 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
364 | Permitting and Engineering (5%) | Nagyantok Outfitting Shop A | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 597500 | 0 | 1 | 0 |  | 0 | 0 | 597500 | 11720 | 1 | - Soft Cost | - Permitting and Engineering
365 | Overall Repair of the Facility | Nagyantok Warehouse | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 650 |  | m2 | 3 | 1 | 1 | 4 | 0.7 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 1137500 | 22310 | 1 | - Container offices for rehabilitation | - Rehabilitation of contatiner offices
366 | Contingencies (10%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 113800 | 0 | 1 | 0 |  | 0 | 0 | 113800 | 2240 | 1 | - Contingencies | 10% contingencies
367 | Preliminaries (10%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 125200 | 0 | 1 | 0 |  | 0 | 0 | 125200 | 2460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
368 | Permitting and Engineering (5%) | Nagyantok Warehouse | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 68900 | 0 | 1 | 0 |  | 0 | 0 | 68900 | 1360 | 1 | - Soft Cost | - Permitting and Engineering
369 | Overall Repair of the Facility | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 360 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1800000 | 35300 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
370 | Contingencies (10%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
371 | Preliminaries (10%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
372 | Permitting and Engineering (5%) | Nagyantok Stock Room 1 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
373 | Overall Repair of the Facility | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 300 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1500000 | 29420 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
374 | Contingencies (10%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | - Contingencies | 10% contingencies
375 | Preliminaries (10%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
376 | Permitting and Engineering (5%) | Nagyantok Stock Room 2 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Soft Cost | - Permitting and Engineering
377 | Overall Repair of the Facility | Nagyantok Stock office | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2016 | 60 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 300000 | 5890 | 1 | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab | - Cleaning of the area - Shower and comfort rooms rehabilitation - Container offices rehab
378 | Contingencies (10%) | Nagyantok Stock office | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 30000 | 0 | 1 | 0 |  | 0 | 0 | 30000 | 590 | 1 | - Contingencies | 10% contingencies
379 | Preliminaries (10%) | Nagyantok Stock office | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 33000 | 0 | 1 | 0 |  | 0 | 0 | 33000 | 650 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
380 | Permitting and Engineering (5%) | Nagyantok Stock office | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 18200 | 0 | 1 | 0 |  | 0 | 0 | 18200 | 360 | 1 | - Soft Cost | - Permitting and Engineering
381 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
382 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 42400 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 187500 | 3680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
383 | Repainting of Walls 2nd Floor | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 187500 | 3680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
384 | Repainting of Walls 1st Floor | Field Office 11B | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 750 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 187500 | 3680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
385 | Replacement of Ceiling Boards | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 780000 | 15300 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
385 | Replacement of Ceiling Boards | Field Office 11B | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1300 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 780000 | 15300 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 4485000 | 87950 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
386 | Replacement of DX type units | Field Office 11B | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 65 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 8970000 | 175890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
387 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 11B | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
388 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 11B | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1300 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2600000 | 50990 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
389 | Repair of roofs and gutters | Field Office 11B | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 11800 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
390 | Miscellaneous items | Field Office 11B | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1543200 | 0 | 1 | 0 |  | 0 | 0 | 1543200 | 30260 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - damaged ceilings - Stained/Rusted Aluminum Glass Door | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Repair of damage ceiling - Restoration stained/rusted aluminum glass door
391 | Contingencies (10%) | Field Office 11B | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2083400 | 0 | 1 | 0 |  | 0 | 0 | 2083400 | 40860 | 1 | - Contingencies | 10% contingencies
392 | Preliminaries (10%) | Field Office 11B | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2291700 | 0 | 1 | 0 |  | 0 | 0 | 2291700 | 44940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
393 | Permitting and Engineering (5%) | Field Office 11B | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1260500 | 0 | 1 | 0 |  | 0 | 0 | 1260500 | 24720 | 1 | - Soft Cost | - Permitting and Engineering
394 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 253500 | 4980 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
395 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 253500 | 4980 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 36100 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 108750 | 2140 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
396 | Repainting of Walls 2nd Floor | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 108750 | 2140 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
397 | Repainting of Walls 1st Floor | Field Office 11A | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 435 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 108750 | 2140 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
398 | Replacement of Ceiling Boards | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 507000 | 9950 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
398 | Replacement of Ceiling Boards | Field Office 11A | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 845 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 507000 | 9950 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2967000 | 58180 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5934000 | 116360 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5934000 | 116360 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
399 | Replacement of DX type units | Field Office 11A | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 43 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5934000 | 116360 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
400 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 11A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 845000 | 16570 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
401 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 11A | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 845 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1690000 | 33140 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
402 | Repair of roofs and gutters | Field Office 11A | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 10000 | 0 | 0 | 0 | - no damages found on the roof aside from the broken downspout which is included in the miscellaneous expenses | - No Capex will be allocated to Phase 2
403 | Miscellaneous items | Field Office 11A | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1013400 | 0 | 1 | 0 |  | 0 | 0 | 1013400 | 19880 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
404 | Contingencies (10%) | Field Office 11A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1368100 | 0 | 1 | 0 |  | 0 | 0 | 1368100 | 26830 | 1 | - Contingencies | 10% contingencies
405 | Preliminaries (10%) | Field Office 11A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1504900 | 0 | 1 | 0 |  | 0 | 0 | 1504900 | 29510 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
406 | Permitting and Engineering (5%) | Field Office 11A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 827700 | 0 | 1 | 0 |  | 0 | 0 | 827700 | 16230 | 1 | - Soft Cost | - Permitting and Engineering
407 | Panel Boards | Sub Station #30 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
408 | Transformers repair | Sub Station #30 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
409 | Overall Repair of the facility | Sub Station #30 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 890 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 890000 | 17460 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
410 | Contingencies (10%) | Sub Station #30 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 139000 | 0 | 1 | 0 |  | 0 | 0 | 139000 | 2730 | 1 | - Contingencies | 10% contingencies
411 | Preliminaries (10%) | Sub Station #30 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 152900 | 0 | 1 | 0 |  | 0 | 0 | 152900 | 3000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
412 | Permitting and Engineering (5%) | Sub Station #30 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84100 | 0 | 1 | 0 |  | 0 | 0 | 84100 | 1650 | 1 | - Soft Cost | - Permitting and Engineering
413 | Panel Boards | Sub Station #24 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
414 | Transformers repair | Sub Station #24 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
415 | Overall Repair of the facility | Sub Station #24 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 340 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 340000 | 6670 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
416 | Contingencies (10%) | Sub Station #24 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 84000 | 0 | 1 | 0 |  | 0 | 0 | 84000 | 1650 | 1 | - Contingencies | 10% contingencies
417 | Preliminaries (10%) | Sub Station #24 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 92400 | 0 | 1 | 0 |  | 0 | 0 | 92400 | 1820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
418 | Permitting and Engineering (5%) | Sub Station #24 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 50900 | 0 | 1 | 0 |  | 0 | 0 | 50900 | 1000 | 1 | - Soft Cost | - Permitting and Engineering
419 | Upgrade to comply current structural code | Panel Shop | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 54983 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1586040 | 54983000 | 1078100 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
420 | Replacement of polycarbornate Roof and Wall | Panel Shop | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 54983 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1099660 | 21570 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
420 | Replacement of polycarbornate Roof and Wall | Panel Shop | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 54983 |  | m2 | 1 | 1 | 1 | 8 | 0.25 | 2000 | 25 | 1 | 14 |  | 1 | 2643400 | 27491500 | 539050 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
421 | Panel Boards | Panel Shop | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 3777060 | 25 | 0 | 11 |  | 1 | 74060 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
422 | Miscellaneous Items | Panel Shop | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 5608300 | 0 | 1 | 0 |  | 0 | 0 | 5608300 | 109970 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
423 | Contingencies (10%) | Panel Shop | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6169100 | 0 | 1 | 0 |  | 0 | 0 | 6169100 | 120970 | 1 | - Contingencies | 10% contingencies
424 | Preliminaries (10%) | Panel Shop | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 6786100 | 0 | 1 | 0 |  | 0 | 0 | 6786100 | 133070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
425 | Permitting and Engineering (5%) | Panel Shop | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3732400 | 0 | 1 | 0 |  | 0 | 0 | 3732400 | 73190 | 1 | - Soft Cost | - Permitting and Engineering
426 | Panel Boards | Sub Station #23 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
427 | Transformers repair | Sub Station #23 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
428 | Overall Repair of the facility | Sub Station #23 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 410 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 410000 | 8040 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
429 | Contingencies (10%) | Sub Station #23 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 91000 | 0 | 1 | 0 |  | 0 | 0 | 91000 | 1790 | 1 | - Contingencies | 10% contingencies
430 | Preliminaries (10%) | Sub Station #23 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 100100 | 0 | 1 | 0 |  | 0 | 0 | 100100 | 1970 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
431 | Permitting and Engineering (5%) | Sub Station #23 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 55100 | 0 | 1 | 0 |  | 0 | 0 | 55100 | 1090 | 1 | - Soft Cost | - Permitting and Engineering
432 | Panel Boards | Sub station #22-1 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
433 | Transformers repair | Sub station #22-1 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
434 | Overall Repair of the facility | Sub station #22-1 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 685 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 685000 | 13440 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
435 | Contingencies (10%) | Sub station #22-1 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 118500 | 0 | 1 | 0 |  | 0 | 0 | 118500 | 2330 | 1 | - Contingencies | 10% contingencies
436 | Preliminaries (10%) | Sub station #22-1 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 130400 | 0 | 1 | 0 |  | 0 | 0 | 130400 | 2560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
437 | Permitting and Engineering (5%) | Sub station #22-1 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 71700 | 0 | 1 | 0 |  | 0 | 0 | 71700 | 1410 | 1 | - Soft Cost | - Permitting and Engineering
438 | Upgrade to comply current structural code | Blasting & Painting Shop C | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 15001 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 432730 | 15001000 | 294140 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
439 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop C | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 15001 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 0 | 14 |  | 1 | 721160 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
440 | Panel Boards | Blasting & Painting Shop C | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 1 | 20230 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
441 | Fire Suppression System | Blasting & Painting Shop C | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
442 | Miscellaneous Items | Blasting & Painting Shop C | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1500100 | 0 | 1 | 0 |  | 0 | 0 | 1500100 | 29420 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of sliding door motor gasket
443 | Contingencies (10%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1650200 | 0 | 1 | 0 |  | 0 | 0 | 1650200 | 32360 | 1 | - Contingencies | 10% contingencies
444 | Preliminaries (10%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1815200 | 0 | 1 | 0 |  | 0 | 0 | 1815200 | 35600 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
445 | Permitting and Engineering (5%) | Blasting & Painting Shop C | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 998400 | 0 | 1 | 0 |  | 0 | 0 | 998400 | 19580 | 1 | - Soft Cost | - Permitting and Engineering
446 | Upgrade to comply current structural code | Blasting & Painting Shop D | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 15008 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 432900 | 15008000 | 294280 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
447 | Replacement of polycarbornate Roof and Wall | Blasting & Painting Shop D | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 15008 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 0 | 14 |  | 1 | 721160 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No Capex will be allocated to Phase 2
448 | Panel Boards | Blasting & Painting Shop D | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 1 | 20230 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
449 | Gas port/ Electrical Panel Location Provision of Barricade | Blasting & Painting Shop D | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 18009018 | 25 | 0 | 2 |  | 1 | 353117.65 | 0 | 0 | 0 | - there are no gas ports and electrical panel inside the building | - No Capex will be allocated to Phase 2
450 | Fire Suppression System | Blasting & Painting Shop D | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
451 | Miscellaneous Items | Blasting & Painting Shop D | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1500800 | 0 | 1 | 0 |  | 0 | 0 | 1500800 | 29430 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of sliding door motor gasket
452 | Contingencies (10%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1650900 | 0 | 1 | 0 |  | 0 | 0 | 1650900 | 32380 | 1 | - Contingencies | 10% contingencies
453 | Preliminaries (10%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1816000 | 0 | 1 | 0 |  | 0 | 0 | 1816000 | 35610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
454 | Permitting and Engineering (5%) | Blasting & Painting Shop D | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 998800 | 0 | 1 | 0 |  | 0 | 0 | 998800 | 19590 | 1 | - Soft Cost | - Permitting and Engineering
455 | Upgrade to comply current structural code | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 18983 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 147120 | 18983000 | 372220 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
456 | Replacement of polycarbornate Roof and Wall | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 18983 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 379660 | 7450 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
456 | Replacement of polycarbornate Roof and Wall | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 18983 |  | m2 | 3 | 1 | 1 | 8 | 0.1 | 2000 | 25 | 1 | 14 |  | 1 | 24520 | 3796600 | 74450 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
457 | Panel Boards | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1895670 | 25 | 0 | 11 |  | 1 | 37170 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
458 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3003000 | 25 | 0 | 2 |  | 1 | 649200 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
458 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3003000 | 25 | 1 | 0 |  | 1 |  | 3003000 | 58890 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
459 | Miscellaneous Items | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1936300 | 0 | 1 | 0 |  | 1 | 21800 | 1936300 | 37970 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
460 | Contingencies (10%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2430200 | 0 | 1 | 0 |  | 0 | 0 | 2430200 | 47660 | 1 | - Contingencies | 10% contingencies
461 | Preliminaries (10%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2673300 | 0 | 1 | 0 |  | 0 | 0 | 2673300 | 52420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
462 | Permitting and Engineering (5%) | Pre-Erection Area - Dock 6 (Pre-Erection Shelter A, B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1470300 | 0 | 1 | 0 |  | 0 | 0 | 1470300 | 28830 | 1 | - Soft Cost | - Permitting and Engineering
463 | Upgrade to comply current structural code | Hull Shop B | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 38920 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 342960 | 38920000 | 763140 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
464 | Replacement of polycarbornate Roof and Wall | Hull Shop B | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 38920 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 778400 | 15270 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
464 | Replacement of polycarbornate Roof and Wall | Hull Shop B | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 38920 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 14 |  | 1 | 160170 | 7784000 | 152630 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
465 | Panel Boards | Hull Shop B | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 123760 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
466 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop B | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3276000 | 25 | 0 | 2 |  | 1 | 744500 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
466 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop B | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3276000 | 25 | 1 | 0 |  | 1 |  | 3276000 | 64240 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
467 | Miscellaneous Items | Hull Shop B | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 3969900 | 0 | 1 | 0 |  | 0 | 0 | 3969900 | 77850 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
468 | Contingencies (10%) | Hull Shop B | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4694500 | 0 | 1 | 0 |  | 0 | 0 | 4694500 | 92050 | 1 | - Contingencies | 10% contingencies
469 | Preliminaries (10%) | Hull Shop B | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5163900 | 0 | 1 | 0 |  | 0 | 0 | 5163900 | 101260 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
470 | Permitting and Engineering (5%) | Hull Shop B | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2840200 | 0 | 1 | 0 |  | 0 | 0 | 2840200 | 55700 | 1 | - Soft Cost | - Permitting and Engineering
471 | Removal and Installation of vinyl tiles | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 714750 | 14020 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
472 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 285900 | 5610 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 27000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 129750 | 2550 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
473 | Repainting of Walls 2nd Floor | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 3 | 1 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 129750 | 2550 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
474 | Repainting of Walls 1st Floor | Field Office 8 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 519 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 129750 | 2550 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
475 | Replacement of Ceiling Boards | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 571800 | 11220 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
475 | Replacement of Ceiling Boards | Field Office 8 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 953 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 571800 | 11220 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 3312000 | 64950 | 2 | - Some of the cassettes are already damaged and needs replacement | - remain to reuse the ACCU until the end of life service of the refrigerants
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3312000 | 64950 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
476 | Replacement of DX type units 1st Floor | Field Office 8 | 1 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 6624000 | 129890 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
477 | Replacement of DX type units 2nd Floor | Field Office 8 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 48 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 6624000 | 129890 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
478 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 8 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 48 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 48000 | 950 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
479 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 8 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 953 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1906000 | 37380 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
480 | Repair of roofs and gutters | Field Office 8 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 7500 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
481 | Miscellaneous items | Field Office 8 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1305600 | 0 | 1 | 0 |  | 0 | 0 | 1305600 | 25600 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Repairs of slab
482 | Contingencies (10%) | Field Office 8 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1762500 | 0 | 1 | 0 |  | 0 | 0 | 1762500 | 34560 | 1 | - Contingencies | 10% contingencies
483 | Preliminaries (10%) | Field Office 8 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1938800 | 0 | 1 | 0 |  | 0 | 0 | 1938800 | 38020 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
484 | Permitting and Engineering (5%) | Field Office 8 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1066400 | 0 | 1 | 0 |  | 0 | 0 | 1066400 | 20910 | 1 | - Soft Cost | - Permitting and Engineering
485 | Upgrade to comply current structural code | Assembly shop (B) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 40562 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1170090 | 40562000 | 795340 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
486 | Replacement of polycarbornate Roof and Wall | Assembly shop (B) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 811240 | 15910 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
486 | Replacement of polycarbornate Roof and Wall | Assembly shop (B) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 195010 | 16224800 | 318140 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
487 | Panel Boards | Assembly shop (B) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 123760 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
488 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (B) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 0.7 | 14423500 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
488 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (B) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 0.7 | 14423500 | 25 | 1 | 0 |  | 1 |  | 10096450 | 197970 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
489 | Miscellaneous Items | Assembly shop (B) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2068700 | 0 | 1 | 0 |  | 0 | 0 | 2068700 | 40570 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
490 | Contingencies (10%) | Assembly shop (B) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5353900 | 0 | 1 | 0 |  | 0 | 0 | 5353900 | 104980 | 1 | - Contingencies | 10% contingencies
491 | Preliminaries (10%) | Assembly shop (B) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5889300 | 0 | 1 | 0 |  | 0 | 0 | 5889300 | 115480 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
492 | Permitting and Engineering (5%) | Assembly shop (B) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3239100 | 0 | 1 | 0 |  | 0 | 0 | 3239100 | 63520 | 1 | - Soft Cost | - Permitting and Engineering
493 | Removal and Installation of vinyl tiles | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 607500 | 11920 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
494 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 243000 | 4770 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 34700 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 157500 | 3090 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
495 | Repainting of Walls 2nd Floor | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 157500 | 3090 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
496 | Repainting of Walls 1st Floor | Field Office 6a | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 630 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 157500 | 3090 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
497 | Replacement of Ceiling Boards | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 486000 | 9530 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
497 | Replacement of Ceiling Boards | Field Office 6a | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 810 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 486000 | 9530 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 2829000 | 55480 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 10 |  | 0 | 0 | 5658000 | 110950 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
498 | Replacement of DX type units | Field Office 6a | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 41 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 20 |  | 0 | 0 | 5658000 | 110950 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
499 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 6a | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 810000 | 15890 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
500 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 6a | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 810 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1620000 | 31770 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
501 | Repair of roofs and gutters | Field Office 6a | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 22000 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
502 | Miscellaneous items | Field Office 6a | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 630300 | 0 | 1 | 0 |  | 0 | 0 | 630300 | 12360 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Comfort Room Rehabilitation | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Comfort Room Rehabilitation
503 | Contingencies (10%) | Field Office 6a | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 693400 | 0 | 1 | 0 |  | 0 | 0 | 693400 | 13600 | 1 | - Contingencies | 10% contingencies
504 | Preliminaries (10%) | Field Office 6a | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 762700 | 0 | 1 | 0 |  | 0 | 0 | 762700 | 14960 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
505 | Permitting and Engineering (5%) | Field Office 6a | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 419500 | 0 | 1 | 0 |  | 0 | 0 | 419500 | 8230 | 1 | - Soft Cost | - Permitting and Engineering
506 | Panel Boards | Sub station #11 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
507 | Transformers repair | Sub station #11 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
508 | Provision for the storm drainage | Sub station #11 | 1 | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 100 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 |  | 500000 | 9810 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
509 | Overall Repair of the facility | Sub station #11 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 800 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 800000 | 15690 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
510 | Contingencies (10%) | Sub station #11 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
511 | Preliminaries (10%) | Sub station #11 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
512 | Permitting and Engineering (5%) | Sub station #11 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
513 | Upgrade to comply current structural code | Welding Inspection Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 5000 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 138470 | 5000000 | 98040 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
514 | Replacement of polycarbornate Roof and Wall | Welding Inspection Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 5000 |  | m2 | 3 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 2000000 | 39220 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
515 | Miscellaneous Items | Welding Inspection Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 750000 | 0 | 1 | 0 |  | 0 | 0 | 750000 | 14710 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - repair of steel rung ladder - Installation of missing anchor bolts | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - repair of steel rung ladder - Installation of missing anchor bolts
516 | Contingencies (10%) | Welding Inspection Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 575000 | 0 | 1 | 0 |  | 0 | 0 | 575000 | 11280 | 1 | - Contingencies | 10% contingencies
517 | Preliminaries (10%) | Welding Inspection Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 632500 | 0 | 1 | 0 |  | 0 | 0 | 632500 | 12410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
518 | Permitting and Engineering (5%) | Welding Inspection Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 347900 | 0 | 1 | 0 |  | 0 | 0 | 347900 | 6830 | 1 | - Soft Cost | - Permitting and Engineering
519 | Panel Boards | Sub Station #37 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
520 | Transformers repair | Sub Station #37 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
521 | Overall Repair of the facility | Sub Station #37 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 250 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
522 | Contingencies (10%) | Sub Station #37 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 109800 | 0 | 1 | 0 |  | 0 | 0 | 109800 | 2160 | 1 | - Contingencies | 10% contingencies
523 | Preliminaries (10%) | Sub Station #37 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 120800 | 0 | 1 | 0 |  | 0 | 0 | 120800 | 2370 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
524 | Permitting and Engineering (5%) | Sub Station #37 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 66500 | 0 | 1 | 0 |  | 0 | 0 | 66500 | 1310 | 1 | - Soft Cost | - Permitting and Engineering
525 | Upgrade to comply current structural code | Assembly shelter (6 nos) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 11130 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 685910 | 13356000 | 261890 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
526 | Replacement of polycarbornate Roof and Wall | Assembly shelter (6 nos) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 11130 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2226000 | 43650 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
526 | Replacement of polycarbornate Roof and Wall | Assembly shelter (6 nos) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 40562 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 16224800 | 318140 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
527 | Miscellaneous Items | Assembly shelter (6 nos) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1558200 | 0 | 1 | 0 |  | 0 | 87700 | 1558200 | 30560 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Repair and replacement of buckled members | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Repair and replacement of buckled members
528 | Contingencies (10%) | Assembly shelter (6 nos) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1714100 | 0 | 1 | 0 |  | 0 | 0 | 1714100 | 33610 | 1 | - Contingencies | 10% contingencies
529 | Preliminaries (10%) | Assembly shelter (6 nos) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1885500 | 0 | 1 | 0 |  | 0 | 0 | 1885500 | 36980 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
530 | Permitting and Engineering (5%) | Assembly shelter (6 nos) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1037000 | 0 | 1 | 0 |  | 0 | 0 | 1037000 | 20340 | 1 | - Soft Cost | - Permitting and Engineering
531 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
532 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 129600 | 2550 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 18500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 93750 | 1840 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
533 | Repainting of Walls 2nd Floor | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 93750 | 1840 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
534 | Repainting of Walls 1st Floor | Field Office 3 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 375 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 93750 | 1840 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
535 | Replacement of Ceiling Boards | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 259200 | 5090 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
535 | Replacement of Ceiling Boards | Field Office 3 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 432 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 259200 | 5090 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 3 | 1 | 1 | 5 | 0.5 | 138000 | 10 | 1 | 0 |  | 0 | 0 | 1518000 | 29770 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - Some Cassette of the ACU are damaged and needs to be replaced - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
536 | Replacement of DX type units | Field Office 3 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 22 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 3036000 | 59530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
537 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 3 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 432000 | 8480 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
538 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 3 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 432 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 864000 | 16950 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
539 | Repair of roofs and gutters | Field Office 3 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 432 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 5200 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
540 | Miscellaneous items | Field Office 3 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 524472 | 0 | 1 | 0 |  | 0 | 0 | 524472 | 10290 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
541 | Contingencies (10%) | Field Office 3 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 708100 | 0 | 1 | 0 |  | 0 | 0 | 708100 | 13890 | 1 | - Contingencies | 10% contingencies
542 | Preliminaries (10%) | Field Office 3 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 778900 | 0 | 1 | 0 |  | 0 | 0 | 778900 | 15280 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
543 | Permitting and Engineering (5%) | Field Office 3 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 421900 | 0 | 1 | 0 |  | 0 | 0 | 421900 | 8280 | 1 | - Soft Cost | - Permitting and Engineering
544 | Upgrade to comply current structural code | Pre-Outfitting Shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 8805 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 254000 | 8805000 | 172650 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
545 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 8805 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 176100 | 3460 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
545 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 8805 |  | m2 | 3 | 1 | 1 | 5 | 0.2 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 3522000 | 69060 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
546 | Panel Boards | Pre-Outfitting Shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 6311760 | 25 | 0 | 11 |  | 1 | 19600 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
547 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 832000 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
547 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 832000 | 25 | 1 | 0 |  | 1 |  | 832000 | 16320 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
548 | Miscellaneous Items | Pre-Outfitting Shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 898200 | 0 | 1 | 0 |  | 0 | 0 | 898200 | 17620 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
549 | Contingencies (10%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1071200 | 0 | 1 | 0 |  | 0 | 0 | 1071200 | 21010 | 1 | - Contingencies | 10% contingencies
550 | Preliminaries (10%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1178300 | 0 | 1 | 0 |  | 0 | 0 | 1178300 | 23110 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
551 | Permitting and Engineering (5%) | Pre-Outfitting Shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 648100 | 0 | 1 | 0 |  | 0 | 0 | 648100 | 12710 | 1 | - Soft Cost | - Permitting and Engineering
552 | Panel Boards | Sub station #21 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
553 | Transformers repair | Sub station #21 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
554 | Overall Repair of the facility | Sub station #21 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1300 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 1300000 | 25500 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
555 | Contingencies (10%) | Sub station #21 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 180000 | 0 | 1 | 0 |  | 0 | 0 | 180000 | 3530 | 1 | - Contingencies | 10% contingencies
556 | Preliminaries (10%) | Sub station #21 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 198000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
557 | Permitting and Engineering (5%) | Sub station #21 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 108900 | 0 | 1 | 0 |  | 0 | 0 | 108900 | 2140 | 1 | - Soft Cost | - Permitting and Engineering
558 | Overall Repair of the facility | Steel Stock Yard | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 37275 |  | m2 | 0 | 1 | 1 | 5 | 0.02 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 3727500 | 73090 | 1 | - Soft Cost | - Permitting and Engineering
559 | Contingencies (10%) | Steel Stock Yard | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 372800 | 0 | 1 | 0 |  | 0 | 0 | 372800 | 7310 | 1 | - Contingencies | 10% contingencies
560 | Preliminaries (10%) | Steel Stock Yard | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 410100 | 0 | 1 | 0 |  | 0 | 0 | 410100 | 8050 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
561 | Permitting and Engineering (5%) | Steel Stock Yard | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 225600 | 0 | 1 | 0 |  | 0 | 0 | 225600 | 4430 | 1 | - Soft Cost | - Permitting and Engineering
562 | Panel Boards | Sub Station #16 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
563 | Transformers repair | Sub Station #16 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
564 | Provision for the storm drainage | Sub Station #16 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
565 | Overall Repair of the facility | Sub Station #16 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 360 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 360000 | 7060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
566 | Contingencies (10%) | Sub Station #16 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 121000 | 0 | 1 | 0 |  | 0 | 0 | 121000 | 2380 | 1 | - Contingencies | 10% contingencies
567 | Preliminaries (10%) | Sub Station #16 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 133100 | 0 | 1 | 0 |  | 0 | 0 | 133100 | 2610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
568 | Permitting and Engineering (5%) | Sub Station #16 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 73300 | 0 | 1 | 0 |  | 0 | 0 | 73300 | 1440 | 1 | - Soft Cost | - Permitting and Engineering
569 | Structural Retrofitting and Rehabilitation (Upgrade to Code) | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 10564 |  | m2 | 5 | 3 | 0 | 4 | 1 | 4000 | 0 | 0 | 0 |  | 1 | 730800 | 0 | 0 | 2 | - substantial damaged found on the internal masonries of the building probably due to lack of shear restraining structures | - Full retrofit of the building is required such as - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
570 | Overall Repair of the facility (Building Envelope and interiors) | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Interior | Architectural | Austal | 2006 | 10564 |  | m2 | 5 | 3 | 1 | 4 | 0.5 | 27000 | 0 | 0 | 0 |  | 1 | 2885000 | 0 | 0 | 1 | - During the rehabilitatition, demolish and construct of damaged masonry walls, restoration of paints (interior and exterior),, rehabilitation of ceilings | - demolish and construct of CHB walls - Repainting of walls and ceiling - Restoration of Confort Rooms and Shower Rooms - Replacement of Ceiling boards
571 | Overall Repair of HVAC System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | HVAC | All Disciplines | Austal | 2006 | 529 |  | TR | 5 | 1 | 1 | 5 | 0.7 | 138000 | 30 | 0 | 0 |  | 1 | 35000 | 0 | 0 | 1 | - Most of the cassettes are already damaged and needs to e replaced. - During the rehabilitation, some of the HVAC ductings cannot be used and needs to be replaced | - Removal and replacement of the HVAC system
571 | Overall Repair of HVAC System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | HVAC | All Disciplines | Austal | 2006 | 1 |  | lot | 5 | 1 | 1 | 5 | 1 | 138000 | 30 | 0 | 5 |  | 1 | 1077500 | 0 | 0 | 1 | - due to criticality, this item has been moved to immediate | - CapEx will be moved to immediate in Phase 2
572 | Overall Repair of Electrical System | Production Center 1/Hospital Building/Substation 8 | Lot | SY | Austal | Electrical System | Electrical | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 5 | 0.2 | 3300 | 0 | 0 | 0 |  | 1 | 109700 | 0 | 0 | 1 | -Due to rehabilitation, there will be wires that needs to be remove and replaced - Burnt-out lightings - damaged electrical auxilliaries (flourescent casings, outlets) | - Removal and Replacement of electrical and Auxilliary Wires
573 | Overall Repair of Plumbing | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 5 | 0.4 | 900 | 0 | 0 | 0 |  | 1 | 83800 | 0 | 0 | 1 | - During the rehabilitation, most pipes will need to be removed and replaced | - Removal and replacemnt of plumbing pipes
574 | Overall Repair of Waterproofing Membrane | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Roof | Roof | Austal | 2006 | 3521.3333 |  | m2 | 5 | 1 | 1 | 5 | 1 | 5500 | 25 | 0 | 0 |  | 1 | 410920 | 0 | 0 | 1 | - waterleaks are present inside the building due to the deterioration of the waterproof membrane | - Removal and Replacement of the waterproof membrane
575 | Demolition and Removal of PCC | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Demolition | Building | Austal | 2006 | 10564 |  | m2 | 5 | 1 | 1 | 1 | 1 | 4000 | 0 | 1 | 10 |  | 0 | 0 | 42256000 | 828550 | 3
576 | Contingencies (10%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4225600 | 0 | 1 | 10 |  | 0 | 0 | 4225600 | 82860 | 1 | - Contingencies | 10% contingencies
577 | Preliminaries (10%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4648200 | 0 | 1 | 10 |  | 0 | 0 | 4648200 | 91150 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
578 | Permitting and Engineering (5%) | Production Center 1/Hospital Building/Substation 8 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2556500 | 0 | 1 | 10 |  | 0 | 0 | 2556500 | 50130 | 1 | - Soft Cost | - Permitting and Engineering
579 | Upgrade to comply current structural code | Blasting & Painting Shop B | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 13895 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 403300 | 13895000 | 272460 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
580 | Panel Boards | Blasting & Painting Shop B | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1031730 | 25 | 1 | 11 |  | 0 | 0 | 1031730 | 20230 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
581 | Fire Suppression System | Blasting & Painting Shop B | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 30528600 | 0 | 0 | 0 |  | 1 | 598600 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
582 | Miscellaneous Items | Blasting & Painting Shop B | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1389500 | 0 | 1 | 0 |  | 0 | 0 | 1389500 | 27250 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - repair of motor for roller-up doors | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - repair of motor for roller-up doors
583 | Contingencies (10%) | Blasting & Painting Shop B | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1528500 | 0 | 1 | 0 |  | 0 | 0 | 1528500 | 29980 | 1 | - Contingencies | 10% contingencies
584 | Preliminaries (10%) | Blasting & Painting Shop B | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1681300 | 0 | 1 | 0 |  | 0 | 0 | 1681300 | 32970 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
585 | Permitting and Engineering (5%) | Blasting & Painting Shop B | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1849500 | 0 | 1 | 0 |  | 0 | 0 | 1849500 | 36270 | 1 | - Soft Cost | - Permitting and Engineering
586 | Overall Repair of the facility | Tool Shop | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 985 |  | m2 | 0 | 1 | 1 | 5 | 0.3 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1477500 | 28980 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
587 | Contingencies (10%) | Tool Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147800 | 0 | 1 | 0 |  | 0 | 0 | 147800 | 2900 | 1 | - Contingencies | 10% contingencies
588 | Preliminaries (10%) | Tool Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162600 | 0 | 1 | 0 |  | 0 | 0 | 162600 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
589 | Permitting and Engineering (5%) | Tool Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89400 | 0 | 1 | 0 |  | 0 | 0 | 89400 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
590 | Panel Boards | Sub Station #3 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
591 | Transformers repair | Sub Station #3 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
592 | Provision for the storm drainage | Sub Station #3 | lot | SY | Austal | Plumbing System | Plumbing | Austal | 2006 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
593 | Overall Repair of the facility | Sub Station #3 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 390 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
594 | Contingencies (10%) | Sub Station #3 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 124000 | 0 | 1 | 0 |  | 0 | 0 | 124000 | 2440 | 1 | - Contingencies | 10% contingencies
595 | Preliminaries (10%) | Sub Station #3 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 136400 | 0 | 1 | 0 |  | 0 | 0 | 136400 | 2680 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
596 | Permitting and Engineering (5%) | Sub Station #3 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 75100 | 0 | 1 | 0 |  | 0 | 0 | 75100 | 1480 | 1 | - Soft Cost | - Permitting and Engineering
597 | Panel Boards | Sub Station #10 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
598 | Transformers repair | Sub Station #10 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 | 0 | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
599 | Provision for the storm drainage | Sub Station #10 | lot | SY | Dock 6 | Plumbing System | Plumbing | Dock 6 | 2009 | 70 |  | lm | 5 | 3 | 0 | 6 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 350000 | 6870 | 2 | - Damage PVC downspouts - No proper connection to the main storm drainage system | - Replacement of PVC downspout - Construction of ditch to connect to the main storm drainage system
600 | Overall Repair of the facility | Sub Station #10 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 207 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 207000 | 4060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
601 | Contingencies (10%) | Sub Station #10 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105700 | 0 | 1 | 0 |  | 0 | 0 | 105700 | 2080 | 1 | - Contingencies | 10% contingencies
602 | Preliminaries (10%) | Sub Station #10 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 116300 | 0 | 1 | 0 |  | 0 | 0 | 116300 | 2290 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
603 | Permitting and Engineering (5%) | Sub Station #10 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 64000 | 0 | 1 | 0 |  | 0 | 0 | 64000 | 1260 | 1 | - Soft Cost | - Permitting and Engineering
604 | Overall Repair of the facility | Fire Station | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 225 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 1125000 | 22060 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
605 | Contingencies (10%) | Fire Station | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 141100 | 0 | 1 | 0 |  | 0 | 0 | 141100 | 2770 | 1 | - Contingencies | 10% contingencies
606 | Preliminaries (10%) | Fire Station | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 155300 | 0 | 1 | 0 |  | 0 | 0 | 155300 | 3050 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
607 | Permitting and Engineering (5%) | Fire Station | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170800 | 0 | 1 | 0 |  | 0 | 0 | 170800 | 3350 | 1 | - Soft Cost | - Permitting and Engineering
608 | Upgrade to comply current structural code | Maintenance Shop | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 1500 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 43120 | 1500000 | 29420 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
609 | Miscellaneous Items | Maintenance Shop | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 150000 | 0 | 1 | 0 |  | 0 | 0 | 150000 | 2950 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
610 | Contingencies (10%) | Maintenance Shop | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165000 | 0 | 1 | 0 |  | 0 | 0 | 165000 | 3240 | 1 | - Contingencies | 10% contingencies
611 | Preliminaries (10%) | Maintenance Shop | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 181500 | 0 | 1 | 0 |  | 0 | 0 | 181500 | 3560 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
612 | Permitting and Engineering (5%) | Maintenance Shop | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 99900 | 0 | 1 | 0 |  | 0 | 0 | 99900 | 1960 | 1 | - Soft Cost | - Permitting and Engineering
613 | Upgrade to comply current structural code | Paint Can Stock Area | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 1550 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 44670 | 1550000 | 30400 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
614 | Fire Suppression System | Paint Can Stock Area | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 3462900 | 0 | 0 | 0 |  | 1 | 67900 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
615 | Miscellaneous Items | Paint Can Stock Area | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 155000 | 0 | 1 | 0 |  | 0 | 0 | 155000 | 3040 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
616 | Contingencies (10%) | Paint Can Stock Area | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170500 | 0 | 1 | 0 |  | 0 | 0 | 170500 | 3350 | 1 | - Contingencies | 10% contingencies
617 | Preliminaries (10%) | Paint Can Stock Area | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 187600 | 0 | 1 | 0 |  | 0 | 0 | 187600 | 3680 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
618 | Permitting and Engineering (5%) | Paint Can Stock Area | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 103200 | 0 | 1 | 0 |  | 0 | 0 | 103200 | 2030 | 1 | - Soft Cost | - Permitting and Engineering
619 | Overall Repair of the facility | Waste Matter/Scrap Iron Stock | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 2600 |  | m2 | 0 | 1 | 1 | 5 | 0.3 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 3900000 | 76480 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints
620 | Contingencies (10%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 390000 | 0 | 1 | 0 |  | 0 | 0 | 390000 | 7650 | 1 | - Contingencies | 10% contingencies
621 | Preliminaries (10%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 429000 | 0 | 1 | 0 |  | 0 | 0 | 429000 | 8420 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
622 | Permitting and Engineering (5%) | Waste Matter/Scrap Iron Stock | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 236000 | 0 | 1 | 0 |  | 0 | 0 | 236000 | 4630 | 1 | - Soft Cost | - Permitting and Engineering
623 | Overall Repair of the facility | Barracks - K | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 2600 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.2 | 0 |  | 0 | 0 | 2600000 | 50990 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU
624 | Contingencies (10%) | Barracks - K | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 260000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Contingencies | 10% contingencies
625 | Preliminaries (10%) | Barracks - K | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 286000 | 0 | 1 | 0 |  | 0 | 0 | 286000 | 5610 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
626 | Permitting and Engineering (5%) | Barracks - K | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 157300 | 0 | 1 | 0 |  | 0 | 0 | 157300 | 3090 | 1 | - Soft Cost | - Permitting and Engineering
627 | Overall Repair of the facility | Barracks - Romanian | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 210 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 525000 | 10300 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans
628 | Contingencies (10%) | Barracks - Romanian | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 52500 | 0 | 1 | 0 |  | 0 | 0 | 52500 | 1030 | 1 | - Contingencies | 10% contingencies
629 | Preliminaries (10%) | Barracks - Romanian | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 57800 | 0 | 1 | 0 |  | 0 | 0 | 57800 | 1140 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
630 | Permitting and Engineering (5%) | Barracks - Romanian | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 31800 | 0 | 1 | 0 |  | 0 | 0 | 31800 | 630 | 1 | - Soft Cost | - Permitting and Engineering
631 | Overall Repair of the facility | Barracks - F | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 700 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 1750000 | 34320 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken ACU
632 | Contingencies (10%) | Barracks - F | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175000 | 0 | 1 | 0 |  | 0 | 0 | 175000 | 3440 | 1 | - Contingencies | 10% contingencies
633 | Preliminaries (10%) | Barracks - F | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192500 | 0 | 1 | 0 |  | 0 | 0 | 192500 | 3780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
634 | Permitting and Engineering (5%) | Barracks - F | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105900 | 0 | 1 | 0 |  | 0 | 0 | 105900 | 2080 | 1 | - Soft Cost | - Permitting and Engineering
635 | Overall Repair of the facility | Barracks - J | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 210 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 525000 | 10300 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans
636 | Contingencies (10%) | Barracks - J | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 52500 | 0 | 1 | 0 |  | 0 | 0 | 52500 | 1030 | 1 | - Contingencies | 10% contingencies
637 | Preliminaries (10%) | Barracks - J | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 57800 | 0 | 1 | 0 |  | 0 | 0 | 57800 | 1140 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
638 | Permitting and Engineering (5%) | Barracks - J | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 31800 | 0 | 1 | 0 |  | 0 | 0 | 31800 | 630 | 1 | - Soft Cost | - Permitting and Engineering
639 | Panel Boards | Sub Station #35 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
640 | Transformers repair | Sub Station #35 | 1 | SY | Navy | Electrical System | Electrical | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
641 | Overall Repair of the facility | Sub Station #35 | 1 | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2009 | 260 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
642 | Contingencies (10%) | Sub Station #35 | lot | SY | Navy | Contingencies | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76000 | 0 | 1 | 0 |  | 0 | 0 | 76000 | 1500 | 1 | - Contingencies | 10% contingencies
643 | Preliminaries (10%) | Sub Station #35 | lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
644 | Permitting and Engineering (5%) | Sub Station #35 | lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46000 | 0 | 1 | 0 |  | 0 | 0 | 46000 | 910 | 1 | - Soft Cost | - Permitting and Engineering
645 | Panel Boards | Sub Station #34 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
646 | Transformers repair | Sub Station #34 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
647 | Overall Repair of the facility | Sub Station #34 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 260 |  | m2 | 0 | 1 | 1 | 5 | 1 | 1000 | 0 | 1 | 0 |  | 0 | 0 | 260000 | 5100 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
648 | Contingencies (10%) | Sub Station #34 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 76000 | 0 | 1 | 0 |  | 0 | 0 | 76000 | 1500 | 1 | - Contingencies | 10% contingencies
649 | Preliminaries (10%) | Sub Station #34 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 83600 | 0 | 1 | 0 |  | 0 | 0 | 83600 | 1640 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
650 | Permitting and Engineering (5%) | Sub Station #34 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 46000 | 0 | 1 | 0 |  | 0 | 0 | 46000 | 910 | 1 | - Soft Cost | - Permitting and Engineering
651 | Upgrade to comply current structural code | Assembly Shop (C) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 27025 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 779570 | 21620000 | 423930 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
652 | Replacement of polycarbornate Roof and Wall | Assembly Shop (C) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 27025 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 540500 | 10600 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
652 | Replacement of polycarbornate Roof and Wall | Assembly Shop (C) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 27025 |  | m2 | 3 | 1 | 1 | 5 | 0.5 | 2000 | 25 | 1 | 14 |  | 1 | 129930 | 27025000 | 529910 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
653 | Panel Boards | Assembly Shop (C) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1856400 | 25 | 0 | 11 |  | 1 | 36400 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
654 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly Shop (C) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 858000 | 25 | 0 | 2 |  | 1 | 635900 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
654 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly Shop (C) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 858000 | 25 | 1 | 0 |  | 1 |  | 858000 | 16830 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
655 | Miscellaneous Items | Assembly Shop (C) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2216100 | 0 | 1 | 0 |  | 0 | 0 | 2216100 | 43460 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
656 | Contingencies (10%) | Assembly Shop (C) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2523500 | 0 | 1 | 0 |  | 0 | 0 | 2523500 | 49490 | 1 | - Contingencies | 10% contingencies
657 | Preliminaries (10%) | Assembly Shop (C) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2775900 | 0 | 1 | 0 |  | 0 | 0 | 2775900 | 54430 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
658 | Permitting and Engineering (5%) | Assembly Shop (C) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1526700 | 0 | 1 | 0 |  | 0 | 0 | 1526700 | 29940 | 1 | - Soft Cost | - Permitting and Engineering
659 | Upgrade to comply current structural code | Blasting Shop A | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 5485.2 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 158230 | 4388160 | 86050 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
660 | Panel Boards | Blasting Shop A | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 378420 | 25 | 1 | 14 |  | 1 | 7420 | 378420 | 7420 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 5 | 3 | 1 | 5 | 1 | 140000 | 10 | 1 | 0 |  | 0 | 0 | 280000 | 5500 | 1 | - Floor mounted ACU's not working according to Hanjin operator | - Replacement of AC
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 10 |  | 0 | 0 | 280000 | 5500 | 1 | - life expectancy of HVAC | - Replacement of AC due to life expectancy
661 | Replacement of Floor mounted AC | Blasting Shop A | 1 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 2 |  | no | 0 | 1 | 1 | 8 | 1 | 140000 | 10 | 1 | 20 |  | 0 | 0 | 280000 | 5500 | 1 | - life expectancy of HVAC | - Replacement of AC due to life expectancy
662 | Miscellaneous Items | Blasting Shop A | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1400500 | 0 | 1 | 0 |  | 0 | 0 | 1400500 | 27470 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - replacement of worn rubber protective covers | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - Torn sliding door motor gasket - replacement of worn rubber protective covers
663 | Contingencies (10%) | Blasting Shop A | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 606900 | 0 | 1 | 0 |  | 0 | 0 | 606900 | 11900 | 1 | - Contingencies | 10% contingencies
664 | Preliminaries (10%) | Blasting Shop A | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 667600 | 0 | 1 | 0 |  | 0 | 0 | 667600 | 13100 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
665 | Permitting and Engineering (5%) | Blasting Shop A | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 367200 | 0 | 1 | 0 |  | 0 | 0 | 367200 | 7200 | 1 | - Soft Cost | - Permitting and Engineering
666 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 235500 | 4620 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
667 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 235500 | 4620 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 45200 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 357500 | 7010 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
668 | Repainting of Walls 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 357500 | 7010 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
669 | Repainting of Walls 1st Floor | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1430 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 357500 | 7010 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
670 | Replacement of Ceiling Boards | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 471000 | 9240 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
670 | Replacement of Ceiling Boards | Field Office 12 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 785 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 471000 | 9240 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
671 | Replacement of DX type units 2nd Floor | Field Office 12 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 40 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5520000 | 108240 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
672 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 12 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 785000 | 15400 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
673 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 12 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 785 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1570000 | 30790 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
674 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 12 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 99 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
675 | Repair of roofs and gutters | Field Office 12 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 12500 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
676 | Miscellaneous items | Field Office 12 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 973000 | 0 | 1 | 0 |  | 0 | 0 | 973000 | 19080 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room
677 | Contingencies (10%) | Field Office 12 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1070300 | 0 | 1 | 0 |  | 0 | 0 | 1070300 | 20990 | 1 | - Contingencies | 10% contingencies
678 | Preliminaries (10%) | Field Office 12 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1177400 | 0 | 1 | 0 |  | 0 | 0 | 1177400 | 23090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
679 | Permitting and Engineering (5%) | Field Office 12 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 647600 | 0 | 1 | 0 |  | 0 | 0 | 647600 | 12700 | 1 | - Soft Cost | - Permitting and Engineering
680 | Removal and Installation of vinyl tiles | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 8 | 1 | 750 | 20 | 1 | 6 |  | 0 | 0 | 431250 | 8460 | 1 | - Vinyl tiles life expentancy is 20 yrs | - Removal and Replacement of new vinyl tiles
681 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 172500 | 3390 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 24500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
682 | Repainting of Walls 2nd Floor | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 120000 | 2360 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
683 | Repainting of Walls 1st Floor | Field Office 7 | 1 | SY | Austal | Interior | Architectural | Austal | 2006 | 480 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 120000 | 2360 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
684 | Replacement of Ceiling Boards | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 345000 | 6770 | 1 | - Ceiling boards life expectancy is 15 years | - Replacement of Ceiling Boards due to life expectancy
684 | Replacement of Ceiling Boards | Field Office 7 | 2 | SY | Austal | Interior | Architectural | Austal | 2006 | 575 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 345000 | 6770 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
685 | Replacement of DX type units 2nd Floor | Field Office 7 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2006 | 29 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 4002000 | 78480 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
686 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 7 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 575000 | 11280 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
687 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 7 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 575 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1150000 | 22550 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
688 | Repair of roofs and gutters | Field Office 7 | Lot | SY | Austal | Roof | Roof | Austal | 2006 | 575 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 6800 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
689 | Miscellaneous items | Field Office 7 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 972700 | 0 | 1 | 0 |  | 0 | 0 | 972700 | 19080 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Repair of damaged ceiling - Restoration of comfort rooms and Shower rooms | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures - Cracks on slab - Repair of damaged ceiling - Restoration of comfort rooms and Shower rooms
690 | Contingencies (10%) | Field Office 7 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 745800 | 0 | 1 | 0 |  | 0 | 0 | 745800 | 14630 | 1 | - Contingencies | 10% contingencies
691 | Preliminaries (10%) | Field Office 7 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 820300 | 0 | 1 | 0 |  | 0 | 0 | 820300 | 16090 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
692 | Permitting and Engineering (5%) | Field Office 7 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 451200 | 0 | 1 | 0 |  | 0 | 0 | 451200 | 8850 | 1 | - Soft Cost | - Permitting and Engineering
693 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 379500 | 7450 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
694 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 379500 | 7450 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 43500 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
695 | Repainting of Walls 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
696 | Repainting of Walls 1st Floor | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
697 | Replacement of Ceiling Boards | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 4 |  | 0 | 0 | 759000 | 14890 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
697 | Replacement of Ceiling Boards | Field Office 9 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 1265 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 19 |  | 0 | 0 | 759000 | 14890 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - remain to reuse the ACCU until the end of life service
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
698 | Replacement of DX type units 2nd Floor | Field Office 9 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2009 | 64 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 8832000 | 173180 | 2 | - the building was contructed in 2016. | - replacement of ACCU due to end of service life
699 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 9 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1265000 | 24810 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
700 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 9 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1265 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2530000 | 49610 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
701 | Rehabilitation of Comfort Rooms and Shower Rooms | Field Office 9 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2009 | 99 |  | m2 | 4 | 3 | 1 | 4 | 1 | 2000 | 0 | 1 | 0 |  | 0 | 0 | 198000 | 3890 | 1 | - all comfort rooms are in poor condition - Stained Floor tiles, damaged dividers, damaged ceilings and cracked water closet | - Rehabilitation of comfort rooms and shower rooms to retain its as-built condition
702 | Repair of roofs and gutters | Field Office 9 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 845 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 12100 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
703 | Miscellaneous items | Field Office 9 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1533300 | 0 | 1 | 0 |  | 0 | 0 | 1533300 | 30070 | 1 | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures -replacement of carpet tiles at meeting room - rehabilitation of comfort room
704 | Contingencies (10%) | Field Office 9 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1686700 | 0 | 1 | 0 |  | 0 | 0 | 1686700 | 33080 | 1 | - Contingencies | 10% contingencies
705 | Preliminaries (10%) | Field Office 9 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1855300 | 0 | 1 | 0 |  | 0 | 0 | 1855300 | 36380 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
706 | Permitting and Engineering (5%) | Field Office 9 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1020500 | 0 | 1 | 0 |  | 0 | 0 | 1020500 | 20010 | 1 | - Soft Cost | - Permitting and Engineering
707 | Overall Repair of the facility | Filtration Plant | 1 | NY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 350 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 1 | 2 |  | 1 | 8900 | 1750000 | 34320 | 1 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door
708 | Contingencies (10%) | Filtration Plant | lot | NY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175000 | 0 | 1 | 2 |  | 0 | 0 | 175000 | 3440 | 1 | - Contingencies | 10% contingencies
709 | Preliminaries (10%) | Filtration Plant | lot | NY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 192500 | 0 | 1 | 2 |  | 0 | 0 | 192500 | 3780 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
710 | Permitting and Engineering (5%) | Filtration Plant | lot | NY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105900 | 0 | 1 | 2 |  | 0 | 0 | 105900 | 2080 | 1 | - Soft Cost | - Permitting and Engineering
711 | Upgrade to comply current structural code | Assembly shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 27390 |  | m2 | 0 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.25 | 0 |  | 0 | 537350 | 27390000 | 537060 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
712 | Replacement of polycarbornate Roof and Wall | Assembly shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 27390 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1643400 | 32230 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
712 | Replacement of polycarbornate Roof and Wall | Assembly shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 27390 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 12 |  | 1 | 89600 | 16434000 | 322240 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
713 | Panel Boards | Assembly shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 3134460 | 25 | 0 | 12 |  | 1 | 61460 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
714 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 0 | 2 |  | 0 | 0 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
714 | Gas port/ Electrical Panel Location Provision of Barricade | Assembly shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 1 | 0 |  | 0 | 0 | 3718000 | 72910 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
715 | Miscellaneous Items | Assembly shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2903400 | 0 | 1 | 0 |  | 0 | 0 | 2903400 | 56930 | 1 | Miscellaneous item includes: - connecting downspout to nearest drainage - repainting - fire extinguisher - cleaning and hauling | Miscellaneous item includes: - connecting downspout to nearest drainage - repainting - fire extinguisher - cleaning and hauling
716 | Contingencies (10%) | Assembly shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3565500 | 0 | 1 | 0 |  | 0 | 0 | 3565500 | 69920 | 1 | - Contingencies | 10% contingencies
717 | Preliminaries (10%) | Assembly shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3922100 | 0 | 1 | 0 |  | 0 | 0 | 3922100 | 76910 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
718 | Permitting and Engineering (5%) | Assembly shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2157200 | 0 | 1 | 0 |  | 0 | 0 | 2157200 | 42300 | 1 | - Soft Cost | - Permitting and Engineering
719 | Upgrade to comply current structural code | Hull Shop (A) | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 37736 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 1291740 | 37736000 | 739930 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
720 | Replacement of polycarbornate Roof and Wall | Hull Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 37736 |  | m2 | 3 | 1 | 1 | 5 | 0.035 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2641520 | 51800 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
720 | Replacement of polycarbornate Roof and Wall | Hull Shop (A) | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 37736 |  | m2 | 3 | 1 | 1 | 5 | 0.3 | 2000 | 25 | 1 | 11 |  | 1 | 215290 | 22641600 | 443960 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
721 | Panel Boards | Hull Shop (A) | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 5369280 | 25 | 0 | 11 |  | 1 | 105280 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
722 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 0 | 2 |  | 1 | 780400 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
722 | Gas port/ Electrical Panel Location Provision of Barricade | Hull Shop (A) | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3718000 | 25 | 1 | 0 |  | 1 |  | 3718000 | 72910 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
723 | Miscellaneous Items | Hull Shop (A) | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 4037800 | 0 | 1 | 0 |  | 0 | 0 | 4037800 | 79180 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
724 | Contingencies (10%) | Hull Shop (A) | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4813400 | 0 | 1 | 0 |  | 0 | 0 | 4813400 | 94390 | 1 | - Contingencies | 10% contingencies
725 | Preliminaries (10%) | Hull Shop (A) | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 5294700 | 0 | 1 | 0 |  | 0 | 0 | 5294700 | 103820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
726 | Permitting and Engineering (5%) | Hull Shop (A) | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2912100 | 0 | 1 | 0 |  | 0 | 0 | 2912100 | 57100 | 1 | - Soft Cost | - Permitting and Engineering
727 | Upgrade to comply current structural code | Powerplant and Control Station | 1 | NY | JV | Structural Upgrade | Structural | Shared | 2006 | 1100 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.5 | 0 |  | 1 | 88840 | 2200000 | 43140 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 3 | 1 | 4 | 0.85 | 2500 | 0 | 1 | 0 |  | 0 | 0 | 2337500 | 45840 | 1 | - replacement of roof due to damage | - Replacement of roof
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 4 | 1 | 2500 | 0 | 0 | 3 |  | 0 | 58500 | 0 | 0 | 1 | - due to criticality, repair of slab moved to immediate | - CapEx will be moved to immediate in Phase 2
728 | Repair of Deflected slab | Powerplant and Control Station | 1 | NY | JV | Structural Elements | Structural | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 4 | 1 | 2500 | 0 | 0 | 5 |  | 0 | 58500 | 0 | 0 | 1 | - due to criticality, repair of slab moved to immediate | - CapEx will be moved to immediate in Phase 2
729 | Overall Repair of Waterproofing Membrane | Powerplant and Control Station | 1 | NY | JV | Roof | Roof | Shared | 2006 | 1100 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2500 | 25 | 1 | 0 |  | 1 | 65500 | 2750000 | 53930 | 1 | - waterleaks are present inside the building due to the deterioration of the waterproof membrane | - Removal and Replacement of the waterproof membrane
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 275000 | 5400 | 1 | - Wall paints are stained - Cracked on walls | - Repainting the wall to its as-built condition - Patching and Sealing of crack walls
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 275000 | 5400 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
730 | Repainting of Walls | Powerplant and Control Station | 1 | NY | JV | Interior | Architectural | Shared | 2006 | 1100 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 275000 | 5400 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
731 | Panel Boards | Powerplant and Control Station | 1 | NY | JV | Electrical System | Electrical | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 82110 | 25 | 1 | 11 |  | 1 | 1610 | 82110 | 1610 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
732 | Miscellaneous Items | Powerplant and Control Station | lot | NY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 756300 | 0 | 1 | 0 |  | 0 | 0 | 756300 | 14830 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
733 | Contingencies (10%) | Powerplant and Control Station | lot | NY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 831900 | 0 | 1 | 0 |  | 0 | 0 | 831900 | 16320 | 1 | - Contingencies | 10% contingencies
734 | Preliminaries (10%) | Powerplant and Control Station | lot | NY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 915100 | 0 | 1 | 0 |  | 0 | 0 | 915100 | 17950 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
735 | Permitting and Engineering (5%) | Powerplant and Control Station | lot | NY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 503300 | 0 | 1 | 0 |  | 0 | 0 | 503300 | 9870 | 1 | - Soft Cost | - Permitting and Engineering
736 | Upgrade to comply current structural code | Pre Treatment Shop A | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 4662 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 92015 | 4662000 | 91420 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
737 | Replacement of polycarbornate Roof and Wall | Pre Treatment Shop A | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 4662 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 932400 | 18290 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
738 | Panel Boards | Pre Treatment Shop A | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 4305 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
739 | Gas port/ Electrical Panel Location Provision of Barricade | Pre Treatment Shop A | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3498600 | 25 | 0 | 2 |  | 1 | 68600 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
740 | Miscellaneous Items | Pre Treatment Shop A | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 466200 | 0 | 1 | 0 |  | 0 | 0 | 466200 | 9150 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
741 | Contingencies (10%) | Pre Treatment Shop A | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 512900 | 0 | 1 | 0 |  | 0 | 0 | 512900 | 10060 | 1 | - Contingencies | 10% contingencies
742 | Preliminaries (10%) | Pre Treatment Shop A | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 564200 | 0 | 1 | 0 |  | 0 | 0 | 564200 | 11070 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
743 | Permitting and Engineering (5%) | Pre Treatment Shop A | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 310300 | 0 | 1 | 0 |  | 0 | 0 | 310300 | 6090 | 1 | - Soft Cost | - Permitting and Engineering
744 | Upgrade to comply current structural code | Pre Treatment Shop B | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 3362 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 92015 | 3362000 | 65930 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
745 | Replacement of polycarbornate Roof and Wall | Pre Treatment Shop B | 1 | SY | Austal | Roof | Roof | Dock 6 | 2006 | 3362 |  | m2 | 3 | 1 | 1 | 5 | 0.1 | 2000 | 25 | 1 | 11 |  | 0 | 0 | 672400 | 13190 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
746 | Panel Boards | Pre Treatment Shop B | 1 | SY | Austal | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 4305 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
747 | Gas port/ Electrical Panel Location Provision of Barricade | Pre Treatment Shop B | 1 | SY | Austal | Fire Protection System | Fire Protection | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3498600 | 25 | 0 | 2 |  | 1 | 68600 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
748 | Miscellaneous Items | Pre Treatment Shop B | lot | SY | Austal | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 336200 | 0 | 1 | 0 |  | 0 | 0 | 336200 | 6600 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
749 | Contingencies (10%) | Pre Treatment Shop B | lot | SY | Austal | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 369900 | 0 | 1 | 0 |  | 0 | 0 | 369900 | 7260 | 1 | - Contingencies | 10% contingencies
750 | Preliminaries (10%) | Pre Treatment Shop B | lot | SY | Austal | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 406900 | 0 | 1 | 0 |  | 0 | 0 | 406900 | 7980 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
751 | Permitting and Engineering (5%) | Pre Treatment Shop B | lot | SY | Austal | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 223800 | 0 | 1 | 0 |  | 0 | 0 | 223800 | 4390 | 1 | - Soft Cost | - Permitting and Engineering
752 | Upgrade to comply current structural code | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 5734 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.2 | 0 |  | 1 | 164770 | 4587200 | 89950 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
753 | Repair of GI Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 2140 |  | m2 | 2 | 1 | 1 | 2 | 0.1 | 2500 | 50 | 1 | 0 |  | 0 | 0 | 535000 | 10500 | 1 | - observed that section of roofs has some holes | - repair of roofs
754 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 5734 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 344040 | 6750 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
754 | Replacement of polycarbornate Roof and Wall | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 5734 |  | m2 | 0 | 1 | 1 | 8 | 0.3 | 2000 | 25 | 1 | 14 |  | 1 | 24520 | 3440400 | 67460 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
755 | Panel Boards | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 14 |  | 1 | 7700 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
756 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 988000 | 25 | 0 | 2 |  | 1 | 134400 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
756 | Gas port/ Electrical Panel Location Provision of Barricade | Pre-Outfitting Shop (B) | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 988000 | 25 | 1 | 0 |  | 1 |  | 988000 | 19380 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
757 | Miscellaneous Items | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 546700 | 0 | 1 | 0 |  | 0 | 0 | 546700 | 10720 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
758 | Contingencies (10%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 700100 | 0 | 1 | 0 |  | 0 | 0 | 700100 | 13730 | 1 | - Contingencies | 10% contingencies
759 | Preliminaries (10%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 770200 | 0 | 1 | 0 |  | 0 | 0 | 770200 | 15110 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
760 | Permitting and Engineering (5%) | Pre-Outfitting Shop (B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 423600 | 0 | 1 | 0 |  | 0 | 0 | 423600 | 8310 | 1 | - Soft Cost | - Permitting and Engineering
761 | Overall Repair of the facility | Sewage Treatment Plant | 1 | SY | JV | Miscellaneous | Miscellaneous | Shared | 2006 | 1120 |  | m2 | 0 | 1 | 1 | 5 | 1 | 5000 | 0 | 0.5 | 0 |  | 0 | 0 | 2800000 | 54910 | 2 | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfort tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door - Crack on slab | Miscellaneous item includes: - fire extinguishers - signages - façade and canopy - cleaning and hauling - Restoration of comfor tooms - Replacement of broken exhaust fans - Replacement of Broken Motor of Roll-up door - Repairs on crack slab
762 | Upgrade to comply DAO 2016 | Sewage Treatment Plant | lot | SY | JV | Plumbing System | Civil | Shared | 2006 | 1 |  | lot | 0 | 3 | 0 | 4 | 1 | 10000000 | 0 | 1 | 0 |  | 0 |  | 10000000 | 196080 | 2 | - Upgrade to comply DAO 2016 | - Rehabilitation of the STP to comply DAO 2016
763 | Contingencies (10%) | Sewage Treatment Plant | lot | SY | JV | Contingencies | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 280000 | 0 | 1 | 0 |  | 0 | 0 | 280000 | 5500 | 2 | - Contingencies | 10% contingencies
764 | Preliminaries (10%) | Sewage Treatment Plant | lot | SY | JV | Preliminaries | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1308000 | 0 | 1 | 0 |  | 0 | 0 | 1308000 | 25650 | 2 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
765 | Permitting and Engineering (5%) | Sewage Treatment Plant | lot | SY | JV | Engineering and Management | Soft Cost | Shared | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 719400 | 0 | 1 | 0 |  | 0 | 0 | 719400 | 14110 | 2 | - Soft Cost | - Permitting and Engineering
766 | Upgrade to comply current structural code | Sub Assembly Shop | 1 | SY | Austal | Structural Upgrade | Structural | Austal | 2006 | 15560 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 378400 | 15560000 | 305100 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
767 | Replacement of polycarbornate Roof and Wall | Sub Assembly Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 15560 |  | m2 | 3 | 1 | 1 | 5 | 0.02 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 622400 | 12210 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
767 | Replacement of polycarbornate Roof and Wall | Sub Assembly Shop | 1 | SY | Austal | Roof | Roof | Austal | 2006 | 15560 |  | m2 | 0 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 63070 | 6224000 | 122040 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
768 | Panel Boards | Sub Assembly Shop | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 439110 | 25 | 0 | 11 |  | 1 | 17710 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
769 | Gas port/ Electrical Panel Location Provision of Barricade | Sub Assembly Shop | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 0 | 2 |  | 1 | 143700 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
769 | Gas port/ Electrical Panel Location Provision of Barricade | Sub Assembly Shop | 1 | SY | Austal | Fire Protection System | Fire Protection | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 1 | 0 |  | 1 |  | 3770000 | 73930 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
770 | Miscellaneous Items | Sub Assembly Shop | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1618300 | 0 | 1 | 0 |  | 0 | 0 | 1618300 | 31740 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
771 | Contingencies (10%) | Sub Assembly Shop | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2157100 | 0 | 1 | 0 |  | 0 | 0 | 2157100 | 42300 | 1 | - Contingencies | 10% contingencies
772 | Preliminaries (10%) | Sub Assembly Shop | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2372800 | 0 | 1 | 0 |  | 0 | 0 | 2372800 | 46530 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
773 | Permitting and Engineering (5%) | Sub Assembly Shop | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1305100 | 0 | 1 | 0 |  | 0 | 0 | 1305100 | 25600 | 1 | - Soft Cost | - Permitting and Engineering
774 | Panel Boards | Sub Station #13 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
775 | Transformers repair | Sub Station #13 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
776 | Overall Repair of the facility | Sub Station #13 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 371 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1113000 | 21830 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
777 | Contingencies (10%) | Sub Station #13 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 161300 | 0 | 1 | 0 |  | 0 | 0 | 161300 | 3170 | 1 | - Contingencies | 10% contingencies
778 | Preliminaries (10%) | Sub Station #13 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 177500 | 0 | 1 | 0 |  | 0 | 0 | 177500 | 3490 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
779 | Permitting and Engineering (5%) | Sub Station #13 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 97600 | 0 | 1 | 0 |  | 0 | 0 | 97600 | 1920 | 1 | - Soft Cost | - Permitting and Engineering
780 | Panel Boards | Sub Station #14 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
781 | Transformers repair | Sub Station #14 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
782 | Overall Repair of the facility | Sub Station #14 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 612 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1836000 | 36000 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
783 | Contingencies (10%) | Sub Station #14 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 233600 | 0 | 1 | 0 |  | 0 | 0 | 233600 | 4590 | 1 | - Contingencies | 10% contingencies
784 | Preliminaries (10%) | Sub Station #14 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 257000 | 0 | 1 | 0 |  | 0 | 0 | 257000 | 5040 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
785 | Permitting and Engineering (5%) | Sub Station #14 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 141400 | 0 | 1 | 0 |  | 0 | 0 | 141400 | 2780 | 1 | - Soft Cost | - Permitting and Engineering
786 | Panel Boards | Sub Station #15 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
787 | Transformers repair | Sub Station #15 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
788 | Overall Repair of the facility | Sub Station #15 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 332 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 996000 | 19530 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
789 | Contingencies (10%) | Sub Station #15 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 149600 | 0 | 1 | 0 |  | 0 | 0 | 149600 | 2940 | 1 | - Contingencies | 10% contingencies
790 | Preliminaries (10%) | Sub Station #15 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 164600 | 0 | 1 | 0 |  | 0 | 0 | 164600 | 3230 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
791 | Permitting and Engineering (5%) | Sub Station #15 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90600 | 0 | 1 | 0 |  | 0 | 0 | 90600 | 1780 | 1 | - Soft Cost | - Permitting and Engineering
792 | Panel Boards | Sub Station #36 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
793 | Transformers repair | Sub Station #36 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
794 | Overall Repair of the facility | Sub Station #36 | 1 | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 400 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1200000 | 23530 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
795 | Contingencies (10%) | Sub Station #36 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 170000 | 0 | 1 | 0 |  | 0 | 0 | 170000 | 3340 | 1 | - Contingencies | 10% contingencies
796 | Preliminaries (10%) | Sub Station #36 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 187000 | 0 | 1 | 0 |  | 0 | 0 | 187000 | 3670 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
797 | Permitting and Engineering (5%) | Sub Station #36 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 102900 | 0 | 1 | 0 |  | 0 | 0 | 102900 | 2020 | 1 | - Soft Cost | - Permitting and Engineering
798 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 403800 | 7920 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
799 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 403800 | 7920 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 42000 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
800 | Repainting of Walls 2nd Floor | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 495000 | 9710 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
801 | Repainting of Walls 1st Floor | Field Office 1 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1980 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 495000 | 9710 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
802 | Replacement of Ceiling Boards | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 807600 | 15840 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
802 | Replacement of Ceiling Boards | Field Office 1 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1346 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 807600 | 15840 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 9384000 | 184000 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 9384000 | 184000 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
803 | Replacement of DX type units | Field Office 1 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 68 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 9384000 | 184000 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
804 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 1 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1346000 | 26400 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
805 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 1 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 1346 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2692000 | 52790 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
806 | Repair of roofs and gutters | Field Office 1 | Lot | SY | Austal | Roof | Roof | Austal | 2008 | 1346 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 11700 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
807 | Miscellaneous items | Field Office 1 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1602800 | 0 | 1 | 0 |  | 0 | 0 | 1602800 | 31430 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
808 | Contingencies (10%) | Field Office 1 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1763000 | 0 | 1 | 0 |  | 0 | 0 | 1763000 | 34570 | 1 | - Contingencies | 10% contingencies
809 | Preliminaries (10%) | Field Office 1 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1939300 | 0 | 1 | 0 |  | 0 | 0 | 1939300 | 38030 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
810 | Permitting and Engineering (5%) | Field Office 1 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1066700 | 0 | 1 | 0 |  | 0 | 0 | 1066700 | 20920 | 1 | - Soft Cost | - Permitting and Engineering
811 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 323700 | 6350 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
812 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 323700 | 6350 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 32100 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 518750 | 10180 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
813 | Repainting of Walls 2nd Floor | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 518750 | 10180 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
814 | Repainting of Walls 1st Floor | Field Office 10 | 1 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 2075 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 518750 | 10180 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
815 | Replacement of Ceiling Boards | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 647400 | 12700 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
815 | Replacement of Ceiling Boards | Field Office 10 | 2 | SY | Dock 6 | Interior | Architectural | Dock 6 | 2008 | 1079 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 647400 | 12700 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 7452000 | 146120 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 7452000 | 146120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
816 | Replacement of DX type units | Field Office 10 | 2 | SY | Dock 6 | HVAC | Mechanical | Dock 6 | 2008 | 54 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 7452000 | 146120 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
817 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 10 | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 1079000 | 21160 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
818 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 10 | 2 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2008 | 1079 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 2158000 | 42320 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
819 | Repair of roofs and gutters | Field Office 10 | Lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2008 | 1079 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 8900 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
820 | Miscellaneous items | Field Office 10 | Lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1302200 | 0 | 1 | 0 |  | 0 | 0 | 1302200 | 25540 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
821 | Contingencies (10%) | Field Office 10 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1432400 | 0 | 1 | 0 |  | 0 | 0 | 1432400 | 28090 | 1 | - Contingencies | 10% contingencies
822 | Preliminaries (10%) | Field Office 10 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1575600 | 0 | 1 | 0 |  | 0 | 0 | 1575600 | 30900 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
823 | Permitting and Engineering (5%) | Field Office 10 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 866600 | 0 | 1 | 0 |  | 0 | 0 | 866600 | 17000 | 1 | - Soft Cost | - Permitting and Engineering
824 | Re-application of Rubberized Floor Paints 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 234000 | 4590 | 1 | - Rubberized paint of the 2nd floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
825 | Re-application of Rubberized Floor Paints 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 300 | 10 | 1 | 0 |  | 0 | 0 | 234000 | 4590 | 1 | - Rubberized paint of the 1st floor is already peeled-off and dilapidated | -Re-application of Rubberized flooring to as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 0 | 2 |  | 1 | 9600 | 0 | 0 | 0 | - Wall paints are stained - Wall paints already reached its end of | - painting of the wall will be moved to immediate to retain its as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 391500 | 7680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
826 | Repainting of Walls 2nd Floor | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 3 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 391500 | 7680 | 1 | - Wall paints are stained - Wall paints already reached its end of | - Repainting the wall to its as-built condition
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
827 | Repainting of Walls 1st Floor | Field Office 6 | 1 | SY | Austal | Interior | Architectural | Austal | 2008 | 1566 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 391500 | 7680 | 1 | - life expectancy of paints | - Repainting of wall due to life expectancy
828 | Replacement of Ceiling Boards | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 3 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 3 |  | 0 | 0 | 468000 | 9180 | 1 | - Ceiling board will already reach its life expectancy of 15 years | - Replacement and Installation of new ceiling boards due to end of life
828 | Replacement of Ceiling Boards | Field Office 6 | 2 | SY | Austal | Interior | Architectural | Austal | 2008 | 780 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 468000 | 9180 | 1 | - life expectancy of ceiling boards | - Installation of new ceiling boards
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 3 | 1 | 1 | 5 | 1 | 138000 | 10 | 1 | 5 |  | 0 | 0 | 5382000 | 105530 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - remain to reuse the ACCU until the end of life service of the refrigerants
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 15 |  | 0 | 0 | 5382000 | 105530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
829 | Replacement of DX type units | Field Office 6 | 2 | SY | Austal | HVAC | Mechanical | Austal | 2008 | 39 |  | TR | 0 | 1 | 1 | 8 | 1 | 138000 | 10 | 1 | 25 |  | 0 | 0 | 5382000 | 105530 | 2 | - life expectancy of HVAC | - Replacement of new Air-condition units due to life expectancy
830 | Electrical Works (extension of wirings, outlets including embedments) | Field Office 6 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 1000 | 25 | 1 | 0 |  | 0 | 0 | 780000 | 15300 | 2 | - All wires are messed and are scattered around the places which is a safety concern of tripping | - addition of new wires - wires needs to be embedded to not cause any tripping - addition of new junction outlets to suit office condition
831 | ELV/ Auxillary Works (Structured Cabling, CCTV, FDAS) (replacement of wirings, outlets including embedments) | Field Office 6 | 2 | SY | Austal | Electrical System | Electrical | Austal | 2008 | 780 |  | m2 | 3 | 2 | 1 | 5 | 1 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 1560000 | 30590 | 2 | - All auxiliary wires are in fair good condition but still re-usable - All IT components such as CCTV and ID scanner are not in good condition. -All wires are messed and are scattered around the places which is a safety concern of tripping | - Replacement of auxilliary wirings, cables - Replacement of CCTV and ID Scanner - Auxilliary wires can follow the same electrical wiring route
832 | Repair of roofs and gutters | Field Office 6 | Lot | SY | Austal | Roof | Roof | Austal | 2008 | 780 |  | m2 | 3 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 0 |  | 1 | 6100 | 0 | 0 | 0 | - no damages found on the roof aside from the ruptured downspout which is included in the miscellaneous expenses | - No CapEx will be included in Phase 2
833 | Miscellaneous items | Field Office 6 | Lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 944100 | 0 | 1 | 0 |  | 0 | 0 | 944100 | 18520 | 1 | Miscellaneous items includes the following: - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures | - Allocation for the unforeseen repair/installation such as - fire extinguishers - signages - door knobs - construction of drainages for downspouts - Hauling and Disposal of unused appliances and furnitures
834 | Contingencies (10%) | Field Office 6 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1038600 | 0 | 1 | 0 |  | 0 | 0 | 1038600 | 20370 | 1 | - Contingencies | 10% contingencies
835 | Preliminaries (10%) | Field Office 6 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1142400 | 0 | 1 | 0 |  | 0 | 0 | 1142400 | 22400 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
836 | Permitting and Engineering (5%) | Field Office 6 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 628400 | 0 | 1 | 0 |  | 0 | 0 | 628400 | 12330 | 1 | - Soft Cost | - Permitting and Engineering
837 | Upgrade to comply current structural code | Painting Shop A Ext. | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 10500 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 386990 | 10500000 | 205890 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
838 | Replacement of polycarbornate Roof and Wall | Painting Shop A Ext. | 1 | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10500 |  | m2 | 3 | 1 | 1 | 5 | 1 | 2000 | 25 | 0 | 14 |  | 1 | 644960 | 0 | 0 | 0 | - It is confirmed in the detailed site inspection that this building does not have any polycarbonate roof and wall installed | - No CaPex will be added in the Phase 2
839 | Panel Boards | Painting Shop A Ext. | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 738990 | 25 | 0 | 14 |  | 1 | 14490 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
840 | Gas port/ Electrical Panel Location Provision of Barricade | Painting Shop A Ext. | 1 | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 3770000 | 25 | 0 | 2 |  | 1 | 253100 | 0 | 0 | 0 | - From our thorough study, the buildingis compliant with the latest fire code of the philippines | - No Capex will be allocated to Phase 2
841 | Miscellaneous Items | Painting Shop A Ext. | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1050000 | 0 | 1 | 0 |  | 0 | 0 | 1050000 | 20590 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
842 | Contingencies (10%) | Painting Shop A Ext. | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1155000 | 0 | 1 | 0 |  | 0 | 0 | 1155000 | 22650 | 1 | - Contingencies | 10% contingencies
843 | Preliminaries (10%) | Painting Shop A Ext. | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1270500 | 0 | 1 | 0 |  | 0 | 0 | 1270500 | 24920 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
844 | Permitting and Engineering (5%) | Painting Shop A Ext. | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 698800 | 0 | 1 | 0 |  | 0 | 0 | 698800 | 13710 | 1 | - Soft Cost | - Permitting and Engineering
845 | Panel Boards | Sub Station #9 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
846 | Transformers repair | Sub Station #9 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
847 | Overall Repair of the facility | Sub Station #9 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 360 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1080000 | 21180 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
848 | Contingencies (10%) | Sub Station #9 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 158000 | 0 | 1 | 0 |  | 0 | 0 | 158000 | 3100 | 1 | - Contingencies | 10% contingencies
849 | Preliminaries (10%) | Sub Station #9 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 173800 | 0 | 1 | 0 |  | 0 | 0 | 173800 | 3410 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
850 | Permitting and Engineering (5%) | Sub Station #9 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 95600 | 0 | 1 | 0 |  | 0 | 0 | 95600 | 1880 | 1 | - Soft Cost | - Permitting and Engineering
851 | Panel Boards | Sub station #12 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 1 | 490 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
852 | Transformers repair | Sub station #12 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
853 | Overall Repair of the facility | Sub station #12 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 735 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2205000 | 43240 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
854 | Contingencies (10%) | Sub station #12 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 270500 | 0 | 1 | 0 |  | 0 | 0 | 270500 | 5310 | 1 | - Contingencies | 10% contingencies
855 | Preliminaries (10%) | Sub station #12 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 297600 | 0 | 1 | 0 |  | 0 | 0 | 297600 | 5840 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
856 | Permitting and Engineering (5%) | Sub station #12 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 163700 | 0 | 1 | 0 |  | 0 | 0 | 163700 | 3210 | 1 | - Soft Cost | - Permitting and Engineering
857 | Panel Boards | Sub station #20 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
858 | Transformers repair | Sub station #20 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
859 | Overall Repair of the facility | Sub station #20 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 325 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 975000 | 19120 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
860 | Contingencies (10%) | Sub station #20 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147500 | 0 | 1 | 0 |  | 0 | 0 | 147500 | 2900 | 1 | - Contingencies | 10% contingencies
861 | Preliminaries (10%) | Sub station #20 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162300 | 0 | 1 | 0 |  | 0 | 0 | 162300 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
862 | Permitting and Engineering (5%) | Sub station #20 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89300 | 0 | 1 | 0 |  | 0 | 0 | 89300 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
863 | Panel Boards | Sub station #22 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
864 | Transformers repair | Sub station #22 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
865 | Overall Repair of the facility | Sub station #22 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 760 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2280000 | 44710 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
866 | Contingencies (10%) | Sub station #22 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 278000 | 0 | 1 | 0 |  | 0 | 0 | 278000 | 5460 | 1 | - Contingencies | 10% contingencies
867 | Preliminaries (10%) | Sub station #22 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 305800 | 0 | 1 | 0 |  | 0 | 0 | 305800 | 6000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
868 | Permitting and Engineering (5%) | Sub station #22 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 168200 | 0 | 1 | 0 |  | 0 | 0 | 168200 | 3300 | 1 | - Soft Cost | - Permitting and Engineering
869 | Panel Boards | Sub station #25 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
870 | Transformers repair | Sub station #25 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
871 | Overall Repair of the facility | Sub station #25 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 325 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 975000 | 19120 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
872 | Contingencies (10%) | Sub station #25 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 147500 | 0 | 1 | 0 |  | 0 | 0 | 147500 | 2900 | 1 | - Contingencies | 10% contingencies
873 | Preliminaries (10%) | Sub station #25 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 162300 | 0 | 1 | 0 |  | 0 | 0 | 162300 | 3190 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
874 | Permitting and Engineering (5%) | Sub station #25 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 89300 | 0 | 1 | 0 |  | 0 | 0 | 89300 | 1760 | 1 | - Soft Cost | - Permitting and Engineering
875 | Panel Boards | Sub station #26 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
876 | Transformers repair | Sub station #26 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
877 | Overall Repair of the facility | Sub station #26 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 760 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2280000 | 44710 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
878 | Contingencies (10%) | Sub station #26 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 278000 | 0 | 1 | 0 |  | 0 | 0 | 278000 | 5460 | 1 | - Contingencies | 10% contingencies
879 | Preliminaries (10%) | Sub station #26 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 305800 | 0 | 1 | 0 |  | 0 | 0 | 305800 | 6000 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
880 | Permitting and Engineering (5%) | Sub station #26 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 168200 | 0 | 1 | 0 |  | 0 | 0 | 168200 | 3300 | 1 | - Soft Cost | - Permitting and Engineering
881 | Panel Boards | Sub station #17 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
882 | Transformers repair | Sub station #17 | 1 | SY | Austal | Electrical System | Electrical | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
883 | Overall Repair of the facility | Sub station #17 | 1 | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2006 | 460 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 1380000 | 27060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
884 | Contingencies (10%) | Sub station #17 | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 188000 | 0 | 1 | 0 |  | 0 | 0 | 188000 | 3690 | 1 | - Contingencies | 10% contingencies
885 | Preliminaries (10%) | Sub station #17 | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 206800 | 0 | 1 | 0 |  | 0 | 0 | 206800 | 4060 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
886 | Permitting and Engineering (5%) | Sub station #17 | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 113800 | 0 | 1 | 0 |  | 0 | 0 | 113800 | 2240 | 1 | - Soft Cost | - Permitting and Engineering
887 | Panel Boards | Sub Station #31 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
888 | Transformers repair | Sub Station #31 | 1 | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
889 | Overall Repair of the facility | Sub Station #31 | 1 | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 320 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 960000 | 18830 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
890 | Contingencies (10%) | Sub Station #31 | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 146000 | 0 | 1 | 0 |  | 0 | 0 | 146000 | 2870 | 1 | - Contingencies | 10% contingencies
891 | Preliminaries (10%) | Sub Station #31 | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 160600 | 0 | 1 | 0 |  | 0 | 0 | 160600 | 3150 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
892 | Permitting and Engineering (5%) | Sub Station #31 | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 88400 | 0 | 1 | 0 |  | 0 | 0 | 88400 | 1740 | 1 | - Soft Cost | - Permitting and Engineering
893 | Panel Boards | Sub Station #32 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
894 | Transformers repair | Sub Station #32 | 1 | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
895 | Overall Repair of the facility | Sub Station #32 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 800 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 2400000 | 47060 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
896 | Contingencies (10%) | Sub Station #32 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 290000 | 0 | 1 | 0 |  | 0 | 0 | 290000 | 5690 | 1 | - Contingencies | 10% contingencies
897 | Preliminaries (10%) | Sub Station #32 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 319000 | 0 | 1 | 0 |  | 0 | 0 | 319000 | 6260 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
898 | Permitting and Engineering (5%) | Sub Station #32 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 175500 | 0 | 1 | 0 |  | 0 | 0 | 175500 | 3450 | 1 | - Soft Cost | - Permitting and Engineering
899 | Panel Boards | Sub Station #38 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 24900 | 25 | 1 | 11 |  | 0 | 0 | 24900 | 490 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
900 | Transformers repair | Sub Station #38 | 1 | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 3 | 1 | 500000 | 25 | 1 | 0 |  | 0 |  | 500000 | 9810 | 1 | - Oil leaks are present outside the transformers and needs to be repaired to avoid decreasing its end of life usage | - Repair of oil leakage of transformers
901 | Overall Repair of the facility | Sub Station #38 | 1 | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2006 | 270 |  | m2 | 0 | 1 | 1 | 5 | 1 | 3000 | 0 | 1 | 0 |  | 0 | 0 | 810000 | 15890 | 1 | - Allocation for the overall repair of the facility such as; - expired fire extinguisher - No proper evacuation plan and emergency signages - burnt-out lightings - broken motor of roll-up doors - Missing cross braces | Miscellaneous items such as - Replacement of Fire extinguishers - Installation of Fire safety signages (evacuation plans, fire exits and alarms) - Replacement of burnt-out lightings - Repair/replacement of motor of roller-up door malfunction - Cleaning of the facility - Repair/Installation of missing cross braces
902 | Contingencies (10%) | Sub Station #38 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 131000 | 0 | 1 | 0 |  | 0 | 0 | 131000 | 2570 | 1 | - Contingencies | 10% contingencies
903 | Preliminaries (10%) | Sub Station #38 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 144100 | 0 | 1 | 0 |  | 0 | 0 | 144100 | 2830 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
904 | Permitting and Engineering (5%) | Sub Station #38 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 79300 | 0 | 1 | 0 |  | 0 | 0 | 79300 | 1560 | 1 | - Soft Cost | - Permitting and Engineering
905 | Overall Repair of the Facility | Air Compressed Room - 1 | 1 | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2006 | 1342 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 0.3 | 2 |  | 0 | 0 | 2013000 | 39480 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
906 | Upgrade to comply current structural code | Air Compressed Room - 1 | 1 | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2006 | 1342 |  | m2 | 2 | 1 | 0 | 5 | 1 | 4000 | 0 | 0.3 | 0 |  | 1 | 33320 | 1610400 | 31580 | 2 | - The building was constructed in 2006 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
907 | Contingencies (10%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 362400 | 0 | 1 | 0 |  | 0 | 0 | 362400 | 7110 | 1 | - Contingencies | 10% contingencies
908 | Preliminaries (10%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 398600 | 0 | 1 | 0 |  | 0 | 0 | 398600 | 7820 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
909 | Permitting and Engineering (5%) | Air Compressed Room - 1 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2016 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 219300 | 0 | 1 | 0 |  | 0 | 0 | 219300 | 4300 | 1 | - Soft Cost | - Permitting and Engineering
910 | Overall Repair of the Facility | Samandra - Maintenance Shop/Office | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 1542 |  | m2 | 3 | 1 | 1 | 4 | 1 | 5000 | 0 | 1 | 0 |  | 0 | 0 | 7710000 | 151180 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
911 | Contingencies (10%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 771000 | 0 | 1 | 0 |  | 0 | 0 | 771000 | 15120 | 1 | - Contingencies | 10% contingencies
912 | Preliminaries (10%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 848100 | 0 | 1 | 0 |  | 0 | 0 | 848100 | 16630 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
913 | Permitting and Engineering (5%) | Samandra - Maintenance Shop/Office | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 466500 | 0 | 1 | 0 |  | 0 | 0 | 466500 | 9150 | 1 | - Soft Cost | - Permitting and Engineering
914 | Overall Repair of the Facility | Samandra - Warehouse | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 1650 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 825000 | 16180 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
915 | Contingencies (10%) | Samandra - Warehouse | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 82500 | 0 | 1 | 0 |  | 0 | 0 | 82500 | 1620 | 1 | - Contingencies | 10% contingencies
916 | Preliminaries (10%) | Samandra - Warehouse | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 90800 | 0 | 1 | 0 |  | 0 | 0 | 90800 | 1790 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
917 | Permitting and Engineering (5%) | Samandra - Warehouse | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 50000 | 0 | 1 | 0 |  | 0 | 0 | 50000 | 990 | 1 | - Soft Cost | - Permitting and Engineering
918 | Overall Repair of the Facility | Samandra - Shop B | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
919 | Contingencies (10%) | Samandra - Shop B | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 25000 | 0 | 1 | 0 |  | 0 | 0 | 25000 | 500 | 1 | - Contingencies | 10% contingencies
920 | Preliminaries (10%) | Samandra - Shop B | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27500 | 0 | 1 | 0 |  | 0 | 0 | 27500 | 540 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
921 | Permitting and Engineering (5%) | Samandra - Shop B | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 15200 | 0 | 1 | 0 |  | 0 | 0 | 15200 | 300 | 1 | - Soft Cost | - Permitting and Engineering
922 | Overall Repair of the Facility | Samandra - Container Shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2300 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1150000 | 22550 | 1 | - Damage Rain gutter - Circuit Breaker No Panel box - Vinyl tile dilapidated - Repainting of hand rails/guard rail - Korean socket - No proper drainage of downspout | - Repair of roof gutter - Supply and install of Panel Box - Replacement of vinyl tile - construction of storm drainage
923 | Contingencies (10%) | Samandra - Container Shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 115000 | 0 | 1 | 0 |  | 0 | 0 | 115000 | 2260 | 1 | - Contingencies | 10% contingencies
924 | Preliminaries (10%) | Samandra - Container Shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 126500 | 0 | 1 | 0 |  | 0 | 0 | 126500 | 2490 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
925 | Permitting and Engineering (5%) | Samandra - Container Shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 69600 | 0 | 1 | 0 |  | 0 | 0 | 69600 | 1370 | 1 | - Soft Cost | - Permitting and Engineering
926 | Repair of GI Roof | Catering Center | Roof | NY | Navy | Roof | Roof | Navy | 2006 | 5276 |  | m2 | 3 | 3 | 1 | 5 | 0.3 | 2800 | 50 | 1 | 0 |  | 0 | 0 | 4431840 | 86900 | 1 | Water Leak marks were observed in some areas of the building | - Replacements of sections of roofs in catering center
926 | Repair of GI Roof | Catering Center | Roof | NY | Navy | Roof | Roof | Navy | 2006 | 5276 |  | m2 | 0 | 1 | 1 | 1 | 1 | 2800 | 50 | 0 | 10 |  | 1 | 130390 | 0 | 0 | 0 | - From our thorough study, GI Roof Has a life expectancy of 40 to 70 yrs | - No Capex will be allocated to Phase 2
927 | Replacement of Ceiling Boards | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6186 |  | m2 | 4 | 2 | 1 | 5 | 1 | 600 | 15 | 1 | 1 |  | 0 | 0 | 3711600 | 72780 | 1 | - Sections of the ceiling boards observed water stains | - Replacement of this ceiling boards are necessary - This can be replaced after a year up to life span. Life expentancy of ceiling boards is up to 15yrs-20yrs
927 | Replacement of Ceiling Boards | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6186 |  | m2 | 0 | 1 | 1 | 8 | 1 | 600 | 15 | 1 | 16 |  | 0 | 0 | 3711600 | 72780 | 1 | - Sections of the ceiling boards observed water stains | - Replacement of this ceiling boards are necessary - This can be replaced after a year up to life span. Life expentancy of ceiling boards is up to 15yrs-20yrs
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 4 | 2 | 1 | 5 | 1 | 250 | 10 | 1 | 1 |  | 1 | 74900 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years - Repair can still be moved to any year | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 11 |  | 0 | 0 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
928 | Repainting of Walls | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 3410 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 21 |  | 0 | 0 | 852500 | 16720 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
929 | Replacement of wall tiles | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 4258.8 |  | m2 | 4 | 3 | 1 | 5 | 0.2 | 1500 | 50 | 1 | 0 |  | 0 | 0 | 1277640 | 25060 | 1 | -Sections of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
930 | Replacement of floor tiles | Catering Center | Lot | NY | Navy | Interior | Architectural | Navy | 2006 | 6300 |  | m2 | 4 | 3 | 1 | 5 | 0.3 | 1500 | 50 | 1 | 0 |  | 0 | 0 | 2835000 | 55590 | 1 | -20% of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 50653200 | 15 | 0 | 5 |  | 1 | 993200 | 0 | 0 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. - Replacement of chillers are distributed every 2 years | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 2 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 4 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 5 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 17 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 19 |  | 0 | 0 | 8000000 | 156870 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
931 | HVAC System | Catering Center | Lot | NY | Navy | HVAC | Mechanical | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 20 |  | 0 | 0 | 8000000 | 156870 | 2 | - chillers system to be replaced due to life expectancy | - chillers system to be replaced due to life expectancy
932 | Rehabilitation of storm drainage, HVAC drainage and wastewater drainage system | Catering Center | Lot | NY | Navy | Plumbing System | Plumbing | Navy | 2006 | 6186 |  | m2 | 3 | 2 | 1 | 1 | 0.5 | 500 | 0 | 1 | 3 |  | 1 | 83800 | 1546500 | 30330 | 1 | - Clogging Iin the drainage systems were foreseen due to the exposure of waste coming from the kitchen (e.g. oils, foods and etc.). Water leakage was also observed at the area due to the dispense from Condensate Water Pipes. | - Rehabilitation of Pipe network for HVAC, Storm and Waste water.
933 | Fire Suppression System | Catering Center | Lot | NY | Navy | Fire Protection System | Fire Protection | Navy | 2006 | 1 |  | lot | 3 | 1 | 1 | 1 | 1 | 12214500 | 0 | 0 | 0 |  | 1 | 239500 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
934 | Electrical Panel Boards | Catering Center | Lot | NY | Navy | Electrical System | Electrical | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 838950 | 25 | 1 | 11 |  | 1 | 16450 | 838950 | 16450 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
935 | Miscellaneous items | Catering Center | Lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2006 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 1932800 | 0 | 1 | 0 |  | 0 | 10000 | 1932800 | 37900 | 1 | Miscellaneous item includes: - Lack of fire extinguishers - lack of fire signages - missing switch cover - doors - defective toilet fixtures - joinery, sealants - Dirty tiles and walls - Unused equipment - Dirty AC blowers | - Provision of new switch cover - Replacement of doors - Replacement of toilet fixtures, water closets and lavatories - Joinery works - Cleaning, Hauling and Disposal - Cleaning and repair of AC blowers
936 | Contingencies (10%) | Catering Center | Lot | NY | Navy | Contingencies | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 4058800 | 0 | 1 | 0 |  | 0 | 0 | 4058800 | 79590 | 1 | - Contingencies | 10% contingencies
937 | Preliminaries (10%) | Catering Center | Lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 4464700 | 0 | 1 | 0 |  | 0 | 0 | 4464700 | 87550 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
938 | Permitting and Engineering (5%) | Catering Center | Lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2006 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 2455600 | 0 | 1 | 0 |  | 0 | 0 | 2455600 | 48150 | 1 | - Soft Cost | - Permitting and Engineering
939 | Upgrade to comply current structural code | T-BHD Shelter | lot | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2008 | 11430 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 662310 | 11430000 | 224120 | 2 | - The building was constructed in 2008 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
940 | Replacement of polycarbornate Roof and Wall | T-BHD Shelter | lot | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2008 | 11430 |  | m2 | 3 | 1 | 1 | 5 | 0.01 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 228600 | 4490 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
940 | Replacement of polycarbornate Roof and Wall | T-BHD Shelter | lot | SY | Tenant 3 | Roof | Roof | Tenant 3 | 2008 | 11430 |  | m2 | 0 | 1 | 1 | 8 | 0.2 | 2000 | 25 | 1 | 11 |  | 1 | 110390 | 4572000 | 89650 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
941 | Panel Boards | T-BHD Shelter | lot | SY | Tenant 3 | Electrical System | Electrical | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1577940 | 25 | 0 | 11 |  | 1 | 30940 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
942 | Gas port/ Electrical Panel Location Provision of Barricade | T-BHD Shelter | lot | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2632500 | 25 | 0 | 2 |  | 1 | 540300 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
942 | Gas port/ Electrical Panel Location Provision of Barricade | T-BHD Shelter | lot | SY | Tenant 3 | Fire Protection System | Fire Protection | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2632500 | 25 | 1 | 0 |  | 1 |  | 2632500 | 51620 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
943 | Miscellaneous Items | T-BHD Shelter | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2008 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 1165900 | 0 | 1 | 0 |  | 1 | 16400 | 1165900 | 22870 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
944 | Contingencies (10%) | T-BHD Shelter | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1545700 | 0 | 1 | 0 |  | 0 | 0 | 1545700 | 30310 | 1 | - Contingencies | 10% contingencies
945 | Preliminaries (10%) | T-BHD Shelter | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 1700300 | 0 | 1 | 0 |  | 0 | 0 | 1700300 | 33340 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
946 | Permitting and Engineering (5%) | T-BHD Shelter | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 935200 | 0 | 1 | 0 |  | 0 | 0 | 935200 | 18340 | 1 | - Soft Cost | - Permitting and Engineering
947 | Upgrade to comply current structural code | Welding Shop (B) | lot | SY | Dock 6 | Structural Upgrade | Structural | Dock 6 | 2009 | 10600 |  | m2 | 2 | 1 | 0 | 2 | 1 | 4000 | 0 | 0.25 | 0 |  | 1 | 329870 | 10600000 | 207850 | 2 | - The building was constructed in 2009 and is assumed that the code used was NSCP 2001. - needs to be aligned with the current NSCP 2015 code | - possible retrofitting works due to the alignment to the current code such as: - Steel Thickening - Addition of Cross Brace - Addition of Steel Frame Members
948 | Replacement of polycarbornate Roof and Wall | Welding Shop (B) | lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10600 |  | m2 | 3 | 1 | 1 | 5 | 0.03 | 2000 | 25 | 1 | 0 |  | 0 | 0 | 636000 | 12480 | 1 | - Sections of the polycarbonate roof and wall are deteriorated | - Replacement of deteriorated polycarbonate roof and wall
948 | Replacement of polycarbornate Roof and Wall | Welding Shop (B) | lot | SY | Dock 6 | Roof | Roof | Dock 6 | 2009 | 10600 |  | m2 | 0 | 1 | 1 | 8 | 0.3 | 2000 | 25 | 1 | 14 |  | 1 | 54890 | 6360000 | 124710 | 1 | - life expectancy of this Polycarbonate Roof is 20 to 30 yrs depending on its maintenance. Assumed to replace every 25 yrs due to environment | - Replacement of roof due to end of service life
949 | Panel Boards | Welding Shop (B) | lot | SY | Dock 6 | Electrical System | Electrical | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 1577940 | 25 | 0 | 14 |  | 1 | 15470 | 0 | 0 | 0 | - During the detailed site inspection, we have confirmed that the electrical box only contains power distribution local panel and not a panel board | - No Capex will be allocated to Phase 2
950 | Gas port/ Electrical Panel Location Provision of Barricade | Welding Shop (B) | lot | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2600000 | 25 | 0 | 2 |  | 1 | 269490 | 0 | 0 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
950 | Gas port/ Electrical Panel Location Provision of Barricade | Welding Shop (B) | lot | SY | Dock 6 | Fire Protection System | Fire Protection | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 2600000 | 25 | 1 | 0 |  | 1 |  | 2600000 | 50990 | 2 | - as per our detailed inspection, there are arresters installed in every gas outlets. This will already prevent/explosion. However, in order to further minmize the hazard, a barrier needs to be installed in between the Gasport and the electrical box outlet. | - Installation of Polyvinyl barrier in between the Gasports and electrical panel
951 | Miscellaneous Items | Welding Shop (B) | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 1123600 | 0 | 1 | 0 |  | 0 | 0 | 1123600 | 22040 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
952 | Contingencies (10%) | Welding Shop (B) | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1496000 | 0 | 1 | 0 |  | 0 | 0 | 1496000 | 29340 | 1 | - Contingencies | 10% contingencies
953 | Preliminaries (10%) | Welding Shop (B) | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 1645600 | 0 | 1 | 0 |  | 0 | 0 | 1645600 | 32270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
954 | Permitting and Engineering (5%) | Welding Shop (B) | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 905100 | 0 | 1 | 0 |  | 0 | 0 | 905100 | 17750 | 1 | - Soft Cost | - Permitting and Engineering
955 | Slope Protection | Slope protection | lot | SY | Tenant 3 | Environmental | Structural | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 2550000 | 0 | 1 | 0 |  | 1 | 50000 | 2550000 | 50000 | 2 | - From environmental observation, landslide is prone in the area. Proper protection against landllide is needed. | - Construction of landslide protection
955 | Slope Protection | Slope protection | lot | SY | Tenant 3 | Environmental | Structural | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1530000 | 0 | 1 | 5 |  | 1 | 30000 | 1530000 | 30000 | 2 | - Maintenance of slope protection | - Maintenance of slope protection
956 | Miscellaneous Items | Slope protection | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 255000 | 0 | 1 | 0 |  | 0 | 0 | 255000 | 5000 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
957 | Contingencies (10%) | Slope protection | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 433500 | 0 | 1 | 0 |  | 0 | 0 | 433500 | 8500 | 1 | - Contingencies | 10% contingencies
958 | Preliminaries (10%) | Slope protection | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 476900 | 0 | 1 | 0 |  | 0 | 0 | 476900 | 9360 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
959 | Permitting and Engineering (5%) | Slope protection | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 262300 | 0 | 1 | 0 |  | 0 | 0 | 262300 | 5150 | 1 | - Soft Cost | - Permitting and Engineering
960 | Spill Prevention Kits Tenant 3 | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Environmental | Environmental | Tenant 3 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
961 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
962 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
963 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
964 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Tenant 3 | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
965 | Spill Prevention Kits Austal | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Environmental | Environmental | Austal | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
966 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Miscellaneous | Miscellaneous | Austal | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
967 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Contingencies | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
968 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Preliminaries | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
969 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Austal | lot | SY | Austal | Engineering and Management | Soft Cost | Austal | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
970 | Spill Prevention Kits Dock 6 | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Environmental | Environmental | Dock 6 | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
971 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Miscellaneous | Miscellaneous | Dock 6 | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
972 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Contingencies | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
973 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Preliminaries | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
974 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Dock 6 | lot | SY | Dock 6 | Engineering and Management | Soft Cost | Dock 6 | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
975 | Spill Prevention Kits Navy | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Environmental | Environmental | Navy | 2009 | 1 |  | lot | 2 | 1 | 1 | 2 | 1 | 1657500 | 0 | 1 | 0 |  | 1 | 32500 | 1657500 | 32500 | 1 | - From environmental due diligence oils spills are prone to buildings such as painting shops, gasoline station, oil stock yard and the likes | - Installation of spill prevention kits
976 | Miscellaneous Items | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Miscellaneous | Miscellaneous | Navy | 2009 | 1 |  | lot | 3 | 1 | 1 | 5 | 1 | 165800 | 0 | 1 | 0 |  | 0 | 0 | 165800 | 3260 | 1 | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - deformed steel angle cross brace | Miscellaneous item includes: - façade and canopy - cleaning and hauling - rusted members for repainting - peeled off paints - replacement of steel angle cross braces
977 | Contingencies (10%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Contingencies | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 182400 | 0 | 1 | 0 |  | 0 | 0 | 182400 | 3580 | 1 | - Contingencies | 10% contingencies
978 | Preliminaries (10%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Preliminaries | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 5 | 1 | 200600 | 0 | 1 | 0 |  | 0 | 0 | 200600 | 3940 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
979 | Permitting and Engineering (5%) | Spill Prevention Kits/Secondary Containment Navy | lot | NY | Navy | Engineering and Management | Soft Cost | Navy | 2009 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 110400 | 0 | 1 | 0 |  | 0 | 0 | 110400 | 2170 | 1 | - Soft Cost | - Permitting and Engineering
980 | Upgrade to comply current structural code | Nagyantok Material Store and Bond shop | Lot | SY | Tenant 3 | Structural Upgrade | Structural | Tenant 3 | 2017 | 9850 |  | m2 | 3 | 2 | 0 | 1 | 1 | 4000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | - The building was constructed in 2016. It is assumed that it is compliant with the current NSCP 2015 code | - No Capex will be allocated to Phase 2
981 | Overall Repair of the Facility | Nagyantok Material Store and Bond shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 250000 | 4910 | 1 | Miscellaneous item includes: - damaged rubberized paint - buckled roof purlins - observed minor damages in roofing | Miscellaneous item includes: - repainting of slab with rubberized paint - repair of purlins - replacement of roof sheets - cleaning
982 | Contingencies (10%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 25000 | 0 | 1 | 0 |  | 0 | 0 | 25000 | 500 | 1 | - Contingencies | 10% contingencies
983 | Preliminaries (10%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27500 | 0 | 1 | 0 |  | 0 | 0 | 27500 | 540 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
984 | Permitting and Engineering (5%) | Nagyantok Material Store and Bond shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 15200 | 0 | 1 | 0 |  | 0 | 0 | 15200 | 300 | 1 | - Soft Cost | - Permitting and Engineering
985 | Overall Repair of the Facility | Nagyantok Procurement Storage shop | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2100 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1050000 | 20590 | 1 | Miscellaneous item includes: - rusted purlins and other structural members - damaged purlins | Miscellaneous item includes: - repainting of rusted members - repair of purlins - cleaning
986 | Contingencies (10%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 105000 | 0 | 1 | 0 |  | 0 | 0 | 105000 | 2060 | 1 | - Contingencies | 10% contingencies
987 | Preliminaries (10%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 115500 | 0 | 1 | 0 |  | 0 | 0 | 115500 | 2270 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
988 | Permitting and Engineering (5%) | Nagyantok Procurement Storage shop | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 63600 | 0 | 1 | 0 |  | 0 | 0 | 63600 | 1250 | 1 | - Soft Cost | - Permitting and Engineering
989 | Overall Repair of the Facility | Nagyantok Segragation Area | Lot | SY | Tenant 3 | Miscellaneous | Miscellaneous | Tenant 3 | 2017 | 2500 |  | m2 | 3 | 2 | 1 | 4 | 1 | 5000 | 0 | 0.1 | 0 |  | 0 | 0 | 1250000 | 24510 | 1 | Miscellaneous item includes: - rusted purlins and other structural members - damaged purlins | Miscellaneous item includes: - repainting of rusted members - repair of purlins - cleaning
990 | Contingencies (10%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Contingencies | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 125000 | 0 | 1 | 0 |  | 0 | 0 | 125000 | 2460 | 1 | - Contingencies | 10% contingencies
991 | Preliminaries (10%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Preliminaries | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 137500 | 0 | 1 | 0 |  | 0 | 0 | 137500 | 2700 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
992 | Permitting and Engineering (5%) | Nagyantok Segragation Area | lot | SY | Tenant 3 | Engineering and Management | Soft Cost | Tenant 3 | 2017 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 75700 | 0 | 1 | 0 |  | 0 | 0 | 75700 | 1490 | 1 | - Soft Cost | - Permitting and Engineering
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 4 | 1 | 1 | 5 | 1 | 250 | 10 | 1 | 0 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 10 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
993 | Repainting of Walls | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 1260 |  | m2 | 0 | 1 | 1 | 8 | 1 | 250 | 10 | 1 | 20 |  | 0 | 0 | 315000 | 6180 | 1 | - some walls have visible cracks due to earthquake - in the kitchen area, walls are already stained - life expectancy of paints is up to 10 years | - Repair of wall cracks with patching - Repainting of stained walls - Repainting of walls to retain its as-buil condition
994 | Upgrade to comply current structural code | Guest House | Lot | NY | Navy | Structural Upgrade | Structural | Navy | 2008 | 2870 |  | m2 | 3 | 3 | 0 | 4 | 1 | 4000 | 0 | 0.5 | 0 |  | 1 | 220670 | 5740000 | 112550 | 2
995 | Replacement of wall tiles | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 800 |  | m2 | 4 | 3 | 1 | 5 | 1 | 1500 | 50 | 1 | 0 |  | 1 | 96400 | 1200000 | 23530 | 1 | -Section of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
996 | Replacement of floor tiles | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2610 |  | m2 | 4 | 3 | 1 | 5 | 1 | 1500 | 50 | 1 | 0 |  | 1 | 126800 | 3915000 | 76770 | 1 | -20% of the tiled area on walls are damaged wall maybe also due to earthquake - Some tiles are stained | - 'Replacement of wall tiles to meet as-built condition
997 | HVAC System | Guest House | Lot | NY | Navy | HVAC | Mechanical | Navy | 2008 | 1 |  | lot | 3 | 2 | 1 | 8 | 1 | 8000000 | 15 | 1 | 5 |  | 0 | 0 | 8000000 | 156870 | 2 | - HVAC system uses R-22 and R-123 which will be phase-out by year 2020-2030 referenced to issued Montreal Protocol. - HVAC can still be in use; however, efficiency cannot be maximize due to its condition. | - chillers system to be replaced due to life expectancy and replacement of refrigerant
997 | HVAC System | Guest House | Lot | NY | Navy | HVAC | Mechanical | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 8 | 1 | 8000000 | 15 | 1 | 20 |  | 1 | 466700 | 8000000 | 156870 | 2 | - life expectancy of chillers | - Replacement of chillers
998 | Fire Suppression System | Guest House | Lot | NY | Navy | Fire Protection System | Fire Protection | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 1 | 1 | 5737500 | 0 | 0 | 0 |  | 1 | 112500 | 0 | 0 | 0 | - From our thorough study, the building is compliant with the latest local fire code | - No Capex will be allocated to Phase 2
999 | Replacement of Ceiling Boards | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2870 |  | lot | 4 | 3 | 1 | 5 | 1 | 720 | 15 | 1 | 0 |  | 1 | 101400 | 2066400 | 40520 | 1 | - water stains are found on the ceiling boards - ceiling boards are deteriorated due to water stains | - Replacement of ceiling boards
999 | Replacement of Ceiling Boards | Guest House | Lot | NY | Navy | Interior | Architectural | Navy | 2008 | 2870 |  | lot | 0 | 1 | 1 | 8 | 1 | 720 | 15 | 1 | 15 |  | 1 | 101400 | 2066400 | 40520 | 1 | - water stains are found on the ceiling boards - ceiling boards are deteriorated due to water stains | - Replacement of ceiling boards
1000 | Replacement of Roof | Guest House | Lot | NY | Navy | Roof | Roof | Navy | 2008 | 2870 |  | lot | 4 | 3 | 1 | 4 | 1 | 2800 | 50 | 1 | 0 |  | 1 | 177900 | 8036000 | 157570 | 1 | - According to Hanjin, roofs were damaged due to earthquake - water stains found inside the building due to damaged roof | - replacement of roofs
1001 | Electrical Panel Boards | Guest House | Lot | NY | Navy | Electrical System | Electrical | Navy | 2008 | 1 |  | lot | 4 | 2 | 1 | 5 | 1 | 199920 | 25 | 1 | 11 |  | 1 | 3920 | 199920 | 3920 | 1 | - Panel Boards are to be replaced in 25 years due to it service life; however, this still can be used after its life span depending on the usage and proper maintenance. | - Replacement of Panel Boards due to end of life
1002 | Miscellaneous items | Guest House | Lot | SY | Navy | Miscellaneous | Miscellaneous | Navy | 2008 | 1 |  | lot | 3 | 2 | 1 | 5 | 1 | 2927300 | 0 | 1 | 0 |  | 0 | 19900 | 2927300 | 57400 | 1 | Miscellaneous item includes: - Lack of fire extinguishers - lack of fire signages - missing switch cover - doors - defective toilet fixtures - joinery, sealants - Dirty tiles and walls - Unused equipment - Dirty AC blowers - dilapidated wooden trellis - Damaged Glass wall | - Provision of new switch cover - Replacement of doors - Replacement of toilet fixtures, water closets and lavatories - Joinery works - Cleaning, Hauling and Disposal - Cleaning and repair of AC blowers - Resotration of wooden trellis - Replacement of Glass
1003 | Contingencies (10%) | Guest House | Lot | SY | Navy | Contingencies | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3220000 | 0 | 1 | 0 |  | 0 | 0 | 3220000 | 63140 | 1 | - Contingencies | 10% contingencies
1004 | Preliminaries (10%) | Guest House | Lot | SY | Navy | Preliminaries | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 3542000 | 0 | 1 | 0 |  | 0 | 0 | 3542000 | 69460 | 1 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1005 | Permitting and Engineering (5%) | Guest House | Lot | SY | Navy | Engineering and Management | Soft Cost | Navy | 2008 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 1948100 | 0 | 1 | 0 |  | 0 | 0 | 1948100 | 38200 | 1 | - Soft Cost | - Permitting and Engineering
1006 | Shared Utilities - Electricity | Shared Utilities - Electricity | Lot | NY+SY | JV | Electrical System | Electrical | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 4 | 1 | 1504500 | 0 | 1 | 0 |  | 0 | 0 | 1504500 | 29500 | 3 | - Outdated software | - Software replacement
1007 | Contingencies (10%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 150500 | 0 | 1 | 0 |  | 0 | 0 | 150500 | 2960 | 3 | - Contingencies | 10% contingencies
1008 | Preliminaries (10%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 165500 | 0 | 1 | 0 |  | 0 | 0 | 165500 | 3250 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1009 | Permitting and Engineering (5%) | Shared Utilities - Electricity | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 91100 | 0 | 1 | 0 |  | 0 | 0 | 91100 | 1790 | 3 | - Soft Cost | - Permitting and Engineering
1010 | Shared Utilities - Water | Shared Utilities - Water | Lot | NY+SY | JV | Plumbing System | Civil | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 4 | 1 | 5253000 | 0 | 1 | 0 |  | 0 | 0 | 5253000 | 103000 | 3 | - Intallation of water meters | - Intallation of water meters
1011 | Contingencies (10%) | Shared Utilities - Water | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 525300 | 0 | 1 | 0 |  | 0 | 0 | 525300 | 10300 | 3 | - Contingencies | 10% contingencies
1012 | Preliminaries (10%) | Shared Utilities - Water | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 577900 | 0 | 1 | 0 |  | 0 | 0 | 577900 | 11340 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1013 | Permitting and Engineering (5%) | Shared Utilities - Water | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 317900 | 0 | 1 | 0 |  | 0 | 0 | 317900 | 6240 | 3 | - Soft Cost | - Permitting and Engineering
1014 | Shared Utilities - Fence | Shared Utilities - Fence | Lot | NY+SY | JV | Perimeter Fence | Civil | Shared | 2020 | 9100 |  | lm | 0 | 1 | 1 | 6 | 1 | 30000 | 0 | 1 | 0 |  | 0 | 0 | 273000000 | 5352950 | 3 | - Construction of perimeter fence | - Construction of perimeter fence
1015 | Contingencies (10%) | Shared Utilities - Fence | Lot | NY+SY | JV | Contingencies | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 27300000 | 0 | 1 | 0 |  | 0 | 0 | 27300000 | 535300 | 3 | - Contingencies | 10% contingencies
1016 | Preliminaries (10%) | Shared Utilities - Fence | Lot | NY+SY | JV | Preliminaries | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 30030000 | 0 | 1 | 0 |  | 0 | 0 | 30030000 | 588830 | 3 | - Preliminaries | - Preliminaries - General Requirements -Temporary Facilities
1017 | Permitting and Engineering (5%) | Shared Utilities - Fence | Lot | NY+SY | JV | Engineering and Management | Soft Cost | Shared | 2020 | 1 |  | lot | 0 | 1 | 1 | 9 | 1 | 16516500 | 0 | 1 | 0 |  | 0 | 0 | 16516500 | 323860 | 3 | - Soft Cost | - Permitting and Engineering

## Opex1
Items | (Php/m3/day) | (USD/m3/day)
Water Treatment Plant (WTP) | 5~8 | 0.1~0.15
Sewage Treatment Plant (STP) | 5~7.5 | 0.1~0.14

## Opex2
Items |  | CAPEX |  | annual OPEX
| Civil & Structure | Equipment |  | b
| a | b | c
| 40% | 60%
MEICA
Equipment Cost
Electrical and A&I
STP
Seawage Network

## abr
Abbreviation | Names
JV | Joint Venture
LOS | Level of Services
MS | Microsoft
NSCP | National Structural Code of the Philippines
NY | Northyard
NY+SY | Northyard and Southyard
O&M | Operation & Maintenance
SY | Southyard
TDD | Technical Due Diligence
USD or $ | United States Dollar

## Definitions
Condition State
CS | Description | Possible Intervention
0 |  | Non existent - "this definition was placed by DDD" | Discount factor
1 | Very Good | only planned maintenance is required | 0%
2 | Good, likely new | Minor maintenance required plus planned maintenance
3 | Fair/moderate | Significant maintenance required | Sensitivity Analysis | Value | Remarks
4 | Poor/bad | Significant rehabilitation/replacement required | Probability of Occurance | 1
5 | Very Poor/very bad | Physically unsound and/or beyond rehabilitation, need replacement or alternative renewal
Intervention Type |  |  | Exchange rate USD/Peso | 51
IS | Definition | Explaination
1 | Do Nothing | Do nothing means you don’t do any repair, you just need to do planned maintenance
2 | Minor Repair
3 | Major Repair
4 | Rehabilitation
5 | Replacement
6 | Alternative Renewal
7 | Audit and Testing
8 | Replacement due to Life Expectancy
9 | Soft Cost
Risk | Name
1 | Green | Repair is somehow needed; However, repairs can be done withing above 6 years
2 | Amber | Repair is needed; However, repairs can be done withing 1yr to 6yr span
3 | Red | needs to be repaired immediately; Immediately needs replacement, May impose Health and Safety Risk, Upgrade to Codes
Investigation Period
25 | years
Code Compliance
0 | Non-code compliant
1 | Code-Compliant
Building Requirements
1 | Return to As-built
2 | Arcadis Evaluation
3 | Tenants Requirements

## IS
Type | Definition
1 | Do Nothing
2 | Minor Repair
3 | Major Repair
4 | Rehabilitation
5 | Replacement
6 | Alternative Renewal
7 | Audit and Testing
8 | Replacement due to Life Expectancy
9 | Soft Cost

## risk
Risk | Name | Remarks
1 | Green | Repair is somehow needed; However, repairs can be done withing above 6 years
2 | Amber | Repair is needed; However, repairs can be done withing 1yr to 6yr span
3 | Red | needs to be repaired immediately; Immediately needs replacement, May impose Health and Safety Risk, Upgrade to Codes

## CS
CS | Description | Possible Intervention
0 |  | Non existent
1 | Very Good | only planned maintenance is required
2 | Good, likely new | Minor maintenance required plus planned maintenance
3 | Fair/moderate | Significant maintenance required
4 | Poor/bad | Significant rehabilitation/replacement required
5 | Very Poor/very bad | Physically unsound and/or beyond rehabilitation, need replacement or alternative renewal

## Levels
Area | Floor Level | Tenant | Zone | User | Owner | Operator | Work Type | Disciplines
NY | Roof | Austal | Dock 5 | Navy | JV | DynCorp-NY | All | Architectural
SY | 5 | Navy | Dock 6 | Dock 6 |  | DynCorp-SY | Building Fabric | All Disciplines
NY+SY | 4 | Tenant 3 | Support | Austal |  | Navy | Contingencies | Building
| 3 | Dock 6 | Dry Dock | Tenant 3 |  | Austal | Demolition | Civil
| 2 | JV |  | Shared |  |  | Disposal | Contingencies
| 1 | [5 empty] | Electrical System | Electrical
| B1 | [5 empty] | Environmental | Engineering and Management
| Lot | [5 empty] | Fire Protection System | Environmental
[7 empty] | HVAC | Fire Protection
[7 empty] | Interior | Hydraulic
[7 empty] | Mechanical System | Mechanical
[7 empty] | Miscellaneous | Miscellaneous
[7 empty] | Engineering and Management | Plumbing
[7 empty] | Perimeter Fence | Soft Cost
[7 empty] | Plumbing System | Roof
[7 empty] | Preliminaries | Structural
Roof
Structural Elements
Structural Upgrade
Vertical Transportation

## life
Assets/Components | Life Expectancy
Painting | 10
Ceiling Board | 15
Air-condition (flor mounted, DX type, inverter) | 10
Panel Board | 25
Polycarbonate roof | 25
Electrical Wirings (not exposed to weather) | 50
Electrical Wirings (exposed) | 25
Generator Set | 30
Linoleum | 20
Steel plate | 20
Electrical & Auxillary equipment | 30
Waterproofing | 25
HVAC System | 30
Lifts | 25
Vinyl tiles | 20