## Capex
No | Items | System | Findings | Cause | Operated_by | Vendors | Area | Level | Zone | Facility | Discipline | YearBuilt | S | CO | SE | HE | R | Interventions | IS | Quantity | Unit | InterPer | Cost | Span | Probability | Year | Binary_highrisk | Binary_option | NPV | NPV_HighRisk | NPV_Option | Remarks | Drawing_reference | Picture_reference | Cost Reference
SMC-001 | 537 KVA Diesel Generator | Standby Generator System | 1) At least one major corrective intervention has been reported, however, the cause of the damage was not disclosed. 2.) 30% of the total power were only backed up. 3.) The generators of Party A will not operate if Party B is operating their generator. However, only 1 of the 2 generators of Party B is working, and can only supply 50% of the total load of airport during emergency. 4.) 'Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Damage | Party A | Third Party | Terminal 1 | Arrival | Zone A2 | Generator Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Renewal with bigger size of GENSET to cater the 100% load. | 6 | 2 | no | 1 | 13000000 |  | 1 | 0 | 1 | 0 | 0 | 26000000 | 0 |  |  |  | Cost Database
SMC-002 | 1500L Fuel Tank | Standby Generator System | 1.) Fuel Tank pumping is mannually operated. 2.) Fuel Tank monitoring is manual. 3.) At least one major corrective intervention has been reported, however, the cause of the damage was not disclosed. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Generator Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Installation of sensors and gas leakage montironing devices. | 4 | 2 | no | 1 | 365000 |  | 1 | 0 | 1 | 0 | 0 | 730000 | 0 |  |  |  | Cost Database
SMC-003 | 2.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Renewal of transformer | 6 | 2 | no | 1 | 4950000 |  | 1 | 0 | 1 | 0 | 0 | 9900000 | 0 |  |  |  | Cost Database
SMC-004 | 1 MVA Dry-Type Transformer | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | Routine/regular maintennace | 4 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-005 | 0.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 2 | 4 | 3 | 3 | Renewal of transformer | 6 | 3 | no | 1 | 2560000 |  | 1 | 0 | 1 | 0 | 0 | 7680000 | 0 |  |  |  | Cost Database
SMC-006 | 0.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-007 | 0.3 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 2 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-008 | 0.225 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-009 | 0.1 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-010 | Automatic Transfer Switch | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-011 | Uninterruptible Power Supply | Low Voltage Distribution | 1.) The UPS has thermal issue. Airblasters are being used as alternative cooling equipment. 2.) UPS can provide emergency power to 100% of critical loads such as IT system and security control cameras. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 4 | 4 | 4 | 4 | 3 | Provision of HVAC system inside the UPS room. | 4 | 1 | lot | 1 | 1200000 |  | 1 | 0 | 1 | 0 | 0 | 1200000 | 0
SMC-012 | Uninterruptible Power Supply | Low Voltage Distribution | UPS may be affected with the prolonged lack of cooling. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 4 | 4 | 4 | 4 | 3 | Tests to be conducted on UPS to assess the damage caused by thermal issue. | 7 | 1 | lot | 0.05 | 5400000 |  | 1 | 0 | 1 | 0 | 0 | 270000 | 0
SMC-013 | Battery Charger | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-014 | Power Factor Correction | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Capacitor Banks | 6 | 1 | lot | 1 | 2100000 |  | 1 | 0 | 1 | 0 | 0 | 2100000 | 0 |  |  |  | Cost Database
SMC-015 | LV Switchboards | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Corrective Maintenance were also done on some parts of the switchboard. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of LV Switchboards | 6 | 1 | lot | 1 | 34000000 |  | 1 | 0 | 1 | 0 | 0 | 34000000 | 0 |  |  |  | Cost Database
SMC-016 | Electrical Feeder Cables | Low Voltage Distribution | 1.) 10% were damaged. 2.) There is a risk of not providing adequate level of services due to low reliability because of aging for remaining. | Typhoon Odette "Rai" | Party A | Thirdy Party | Airside | Apron | All Zone | General | Electrical | 1994 | 5 | 4 | 5 | 5 | 3 | Renewal of Electrical Feeder Cables | 6 | 1 | lot | 0.1 | 9700000 |  | 1 | 0 | 1 | 0 | 0 | 970000 | 0 |  |  |  | Cost Database
SMC-017 | Electrical Feeder Cables | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Some cables had undergone replacement during renovation in 2018. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Feeder Cables | 6 | 1 | lot | 1 | 9700000 |  | 1 | 0 | 1 | 0 | 0 | 9700000 | 0 |  |  |  | Cost Database
SMC-018 | Busbars | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Preventive maintenance is performed annually. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Busbars | 6 | 1 | lot | 1 | 20000000 |  | 1 | 0 | 1 | 0 | 0 | 20000000 | 0 |  |  |  | Cost Database
SMC-019 | Cable Trays | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Cable Trays | 6 | 1 | lot | 1 | 14500000 |  | 1 | 0 | 1 | 0 | 0 | 14500000 | 0 |  |  |  | Cost Database
SMC-020 | Normal Lighting | General Lighting and Power System | 1.) 5% of the normal lightings were already busted in North Wing Arrival. 2.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Arrival | Zone B3 | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.05 | 13778800 |  | 1 | 0 | 0 | 0 | 688940 | 0 | 0 |  |  |  | Cost Database
SMC-021 | Normal Lighting | General Lighting and Power System | 1.) 10% of the normal lightings were already busted. 2.) 50% of the lightings were not yet LED. 3.) No spares for Lighting Bulbs & Fixtures. | Damage | Party A | Thirdy Party | Terminal 1 | Departure | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.2 | 13778800 |  | 1 | 0 | 0 | 0 | 2755760 | 0 | 0 |  |  |  | Cost Database
SMC-022 | Normal Lighting | General Lighting and Power System | 1.) 40% of the normal lightings were already busted. 2.) 50% of the lightings were not yet LED. 3.) No spares for Lighting Bulbs & Fixtures. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.2 | 13778800 |  | 1 | 0 | 0 | 0 | 2755760 | 0 | 0 |  |  |  | Cost Database
SMC-023 | Emergency Exit Lights | General Lighting and Power System | 1.)Generally, the emergency lights were not working. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Emergency Exit Lightings | 5 | 1 | lot | 0.3 | 2600000 |  | 1 | 0 | 0 | 0 | 780000 | 0 | 0 |  |  |  | Cost Database
SMC-024 | Directional Signages | General Lighting and Power System | 1.) 90% of the directional signages were damaged. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of directional signages | 5 | 1 | lot | 1 | 2130000 |  | 1 | 0 | 0 | 0 | 2130000 | 0 | 0 |  |  |  | Cost Database
SMC-025 | Carpark Lighting | General Lighting and Power System | 1.) 2-3% of the carpark lighting were damaged. 2.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2010 | 5 | 4 | 5 | 5 | 2 | Replacement of damaged carpark lighting | 5 | 1 | lot | 1 | 1359375 |  | 1 | 0 | 0 | 0 | 1359375 | 0 | 0 |  |  |  | Cost Database
SMC-026 | High Mast Lighting | General Lighting and Power System | 1.) Power supply for 3 fixed pole were damaged. 2.) 6 out of 14 poles had defective lightings. 3.) Controls for High Mast Lighting are manual since BMS is not existing on Terminal 1. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Apron | General | General | Electrical | 2010 | 5 | 4 | 5 | 5 | 2 | Replacement of damaged high mast lights Automation of Monitoring and Control for High Mast Lighting | 5 | 1 | lot | 0.6 | 15312500 |  | 1 | 0 | 0 | 0 | 9187500 | 0 | 0 |  |  |  | Cost Database (8 floodlights per pole)
SMC-027 | Obstruction Lights | General Lighting and Power System | 1.) Obstruction lights are in good condition. |  | Party A | Thirdy Party | Terminal 1 | Apron | General | General | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-028 | Airfield Ground Lighting (by Party B) | General Lighting and Power System | 1.) High possibility of damaged / busted Airfield Ground Lights on runway due to Typhoon Odette. 2.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Typhoon Odette "Rai" | Party BA | Thirdy Party | Airside | Apron | General | General | Electrical | 1994 | 4 | 4 | 3 | 3 | 3 | replacement of airfield ground lighting | 5 | 1 | lot | 0.3 | 13250000 |  | 1 | 0 | 0 | 0 | 3975000 | 0 | 0 |  |  |  | market rate
SMC-029 | Approach Lighting (by Party B) | General Lighting and Power System | 1.) 15% of the Approach Lighting were damaged. 2.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Typhoon Odette "Rai" | Party BA | Thirdy Party | Airside | Apron | General | General | Electrical | 1994 | 4 | 4 | 3 | 3 | 3 | replacement of approach lighting | 5 | 1 | lot | 0.15 | 4875000 |  | 1 | 0 | 0 | 0 | 731250 | 0 | 0 |  |  |  | market rate (5 approach light per pole, total of 13 poles)
SMC-030 | Outlets | General Lighting and Power System | 1.) minor deterioration or damaged on covers of power outlets. | Damage | Party A | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2010 | 3 | 3 | 3 | 4 | 2 | corrective interventon of small power outlets | 2 | 1 | lot | 0.5 | 995000 |  | 1 | 0 | 0 | 0 | 497500 | 0 | 0 |  |  |  | Cost Database
SMC-031 | General Lighting and Power Roughing - Ins and accessories | General Lighting and Power System | 1.) 90% of the junction box were already corroded. 2.) Roughing - Ins tagging were not found on some areas. | Damage | Party A | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2010 | 4 | 4 | 4 | 4 | 3 | corrective interventon of general lighting and power roughing - ins and accessories | 2 | 1 | lot | 0.9 | 505000 |  | 1 | 0 | 0 | 0 | 454500 | 0 | 0 |  |  |  | Cost Database
SMC-032 | Earthing and Lightning Devices | Earthing and Lightning System | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Earth Bars and Grounding System are in good condition. Annual preventive maintenance is conducted. | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 4 | 3 | Renewal of earthing and lightning devices | 6 | 1 | lot | 1 | 4422400 |  | 1 | 0 | 0 | 0 | 4422400 | 0 | 0 |  |  |  | Cost Database
SMC-033 | Solar Panels | Photovoltaic System | 1.) 93 out of 17,000 panels were damaged by the typhoon | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Roof Level | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged solar panels | 5 | 1 | lot | 0.1 | 45000000 |  | 1 | 0 | 0 | 0 | 4500000 | 0 | 0 |  |  |  | Cost Database, percentage loading
SMC-034 | Electrical Feeder Cables | Low Voltage Distribution | 1.) The feeder cables were not fully loaded. Has provision for expansion. 2.) The feeder cables have tagging. |  | Party A | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | Routine/regular maintennace | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-035 | Power Factor Correction | Low Voltage Distribution | 1.) The power factor correction are in good condition. 2.) Annual Preventive Maintenance is conducted. |  | Party A | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-036 | Low Voltage Switchboard | Low Voltage Distribution | 1.) The Swtichboards are in good condition. 2.) Spares and Spaces were found on switchboard. |  | Party A | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-037 | 2.5MVA Dry-Type Transformer | Low Voltage Distribution | 1.) The Transformers are still in good condition. 2.) Annual Preventive Maintenance is conducted. |  | Party A | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-038 | 1.5MVA Diesel Generator | Standby Generator System | 1.) 2 out of 3 Diesel Generator had corrective maintenance due to damages caused by Typhoon Odette. 2.) The Diesel Generator can provide emergency power for 100% load. 3.) Has provision of 1.5MVA for future expansion. 4.) Louver to be upgraded on Genset Room |  | Party A | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance and monitoring | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-039 | 1000L Day Tank | Standby Generator System | 1.) The day tank is still on good condition 2.) The monitoring of fuel level is automated. 3.) The refilling of fuel is automated. |  | Party A | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-040 | 15,000 Mother Tank | Standby Generator System | 1.) The mother tank is still on good condition 2.) The monitoring of fuel level is automated. 3.) The refilling of fuel is automated. |  | Party A | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-041 | Carpark Lighting | General Lighting and Power System | 1.) 30% of carpark Lightings were damaged. 2.) No provions/spare for Lighting Fixtures | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | Replacement of damaged carpark lighting | 5 | 1 | lot | 0.3 | 3171875 |  | 1 | 0 | 0 | 0 | 951562.5 | 0 | 0 |  |  |  | market rate
SMC-042 | Street Lighting | General Lighting and Power System | 1.) 30% of street lighting cover were damaged. 2.) 20% of the street lights were not working. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged street lighting | 5 | 1 | lot | 0.3 | 4531250 |  | 1 | 0 | 0 | 0 | 1359375 | 0 | 0 |  |  |  | assumed 50 street lights
SMC-043 | Directional Signages | General Lighting and Power System | 1.) 10-15% of directional signages were damaged and not working. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged directional signages | 5 | 1 | lot | 0.15 | 270000 |  | 1 | 0 | 0 | 0 | 40500 | 0 | 0
SMC-044 | High Mast Lighting | General Lighting and Power System | 1.) 2 out 11 poles for high mast lightings were already damaged. 2.) 6 out of 11 high mast lightings in terminal 2 had defective lightings. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | Apron | All Zone | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | Replacement of damaged high mast lighting | 5 | 1 | lot | 0.2 | 10312500 |  | 1 | 0 | 0 | 0 | 2062500 | 0 | 0 |  |  |  | Cost Database (8 floodlights per pole)
SMC-045 | Uninterruptible Power Supply | Low Voltage Distribution | 1.) 2 out of 4 UPS were damaged by Typhoon Odette. 2.) The UPS can accommodate 100% load of the critical and IT Systems. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | Arrival | Zone E4 | UPS Room | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | corrective maintenance of damaged UPS | 2 | 4 | no | 0.5 | 2087925 |  | 1 | 0 | 0 | 0 | 4175850 | 0 | 0 |  |  |  | Cost Database
SMC-046 | Outlets | General Lighting and Power System | 1.) Generally, the power outlets are in good condition |  | Party A | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-047 | Normal Lighting | General Lighting and Power System | 1.) 30% of the total architectural lighting were already busted. 2.) Preventive and corrective maintenance of normal lightings is not easily accessible and doable due to high ceilings. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged normal / architectural lightings | 5 | 1 | lot | 0.3 | 20000000 |  | 1 | 0 | 0 | 0 | 6000000 | 0 | 0 |  |  |  | Cost Database
SMC-048 | Junction box and Pull box | General Lighting and Power System | 1.) 20% of the total junction box were uncovered. 2.) 2% of the pullbox enclosure were damaged. | Damage | Party A | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 3 | 3 | 4 | 4 | 2 | replacement of damaged junction box and pull box | 5 | 1 | lot | 0.2 | 600000 |  | 1 | 0 | 0 | 0 | 120000 | 0 | 0 |  |  |  | Cost Database
DDD-001 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Basement | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-004 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-028 | Sprinkler heads and pipes | Fire Protection System | Minor leakages and deterioration are found in the reducer. | Damage | Party A | Thirdy Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 4 | 3 | 4 | 4 | 2 | Repair or replace the deteriorated reducer. | 4 | 1 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 20000 | 0 | 0
DDD-023 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-042 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Departure | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-060 | Portable Fire Extinguisher | Fire Protection System | Carbon Dioxide Portable Fire Extinguisher is in good condition. Its scheduled hydrostatic testing or replacement is near. | Aging | Party A | Thirdy Party | Terminal 2 | Basement | Zone E2 | Pump Room | Mechanical | 2018 | 4 | 4 | 4 | 4 | 2 | Replace the Carbon dioxide portable fire extinguisher on the 5th year or on 2023. | 5 | 57 | unit | 1 | 7550 |  | 1 | 0 | 0 | 0 | 430350 | 0 | 0
VVL-001 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 39 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-103 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 42 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-117 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Departure | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 37 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVL-021 | Fire Hydrant | Fire Protection System | The fire hydrant is generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 15 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-134 | Jockey Pump | Fire Protection System | The jockey pump is generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-135 | Fire Pumps | Fire Protection System | The fire pumps are generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-136 | Fire Tank | Fire Protection System | The fire tank is generally in good condition. |  | Party A | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-137 | Chiller 1 & 2 | MVAC System | Still provide adequate LOS and in good condition |  | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-139 | Chiller 3 | MVAC System | VFD controller and contactor are defective. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 4 | 4 | 3 | 4 | 3 | Repair the VFD controller. | 4 | 1 | unit | 1 | 380000 |  | 1 | 0 | 0 | 0 | 380000 | 0 | 0
DDD-140 | Chiller 4 | MVAC System | Condenser tube is leaking. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 4 | 4 | 3 | 4 | 3 | Repair the condenser tube | 5 | 1 | unit | 1 | 1170000 |  | 1 | 0 | 0 | 0 | 1170000 | 0 | 0
DDD-141 | Cooling Tower 1 to 4 | MVAC System | This can operate but with minor issues such as damaged protective screens and corrosions. | Damage | Party A | Thirdy Party | Terminal 1 | Departure | Zone A2 | Cooling Tower Space | Mechanical | 2012 | 3 | 2 | 3 | 3 | 2 | Repair the protective screens and corrosions. | 3 | 4 | unit | 1 | 87000 |  | 1 | 0 | 0 | 0 | 348000 | 0 | 0
DDD-145 | AHU-NPP1-1, -1, -2, -3 | MVAC System | Insulations are damaged due to typhoon Rai (Odette) but the unit can still operate. | Typhoon Odette "Rai" | Party A | Thirdy Party | Terminal 1 | Roof Level | All Zone | Roofdeck | Mechanical | 2019 | 3 | 2 | 3 | 2 | 3 | Repair the insulations | 3 | 1 | lot | 1 | 140000 |  | 1 | 0 | 0 | 0 | 140000 | 0 | 0 | Damaged by Typhoon Rai
DDD-149 | Safety Issue with the Chiller | MVAC System | The chiller room is also used as storage. 5s is not practiced properly. |  | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 1 | 1 | 1 | 1 | 3 | Clean and practice 5S in the room. | 2 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fire Hazard/Maintenance Issue
DDD-150 | Insulation of chilled water pipes | MVAC System | Deteriorating insulation and molds were observed. | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the insulations | 3 | 1 | lot | 1 | 177900 |  | 1 | 0 | 0 | 0 | 177900 | 0 | 0
DDD-151 | Insulation of air ducts | MVAC System | Deteriorating insulation and molds were observed. | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the insulations | 3 | 1 | lot | 1 | 147000 |  | 1 | 0 | 0 | 0 | 147000 | 0 | 0
DDD-152 | 2 valves | MVAC System | Marks of leakages were found in two valves. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the valves | 3 | 2 | unit | 1 | 449400 |  | 1 | 0 | 0 | 0 | 898800 | 0 | 0
DDD-153 | AHUs | MVAC System | Aging | Aging | Party A | Thirdy Party | Terminal 1 | Arrival | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 4 | 7 | unit | 1 | 500000 |  | 1 | 0 | 1 | 0 | 0 | 3500000 | 0
DDD-158 | Insulation of air ducts | MVAC System | Aging | Aging | Party A | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 3 | 1 | lot | 1 | 147000 |  | 1 | 0 | 1 | 0 | 0 | 147000 | 0
DDD-159 | Insulation of chilled water pipes | MVAC System | Aging | Aging | Party A | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 3 | 1 | lot | 1 | 177900 |  | 1 | 0 | 1 | 0 | 0 | 177900 | 0
DDD-162 | Portable Fire Extinguisher | Fire Protection System | It is estimated that the portable fire extinguishers were not inspected monthly as specified in NFPA 10. | Damage | Party A | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 2019 | 3 | 3 | 3 | 3 | 3 | External and internal inspections of the fire extinguishers are required. Replacement of defective fire extinguishers is most likely. | 3 | 1 | lot | 1 | 25000 |  | 1 | 0 | 0 | 0 | 25000 | 0 | 0
DDD-163 | Fire Protection Pipe Supports | Fire Protection System | Buckling and irregular edges are present in the supports of pipes. | Damage | Party A | Thirdy Party | Terminal 1 | Arrival | Zone E1 | General | Mechanical | 2019 | 3 | 3 | 3 | 3 | 3 | Repair the existing supports and provide additional supports as necessary. | 3 | 1 | lot | 1 | 500000 |  | 1 | 0 | 0 | 0 | 500000 | 0 | 0 | Assumed all supports to be repaired or replaced.
RAS-001 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1384.87 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-002 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Apron | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1384.87 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-003 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1420.77 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-004 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Apron | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1420.77 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-005 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone E2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 647.47 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-006 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Apron | Zone E2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 647.47 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-007 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone E4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 697.8 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-008 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1502.34 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-009 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Apron | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1502.34 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-010 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1464.13 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-011 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 490.23 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-012 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1591.09 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-013 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 536.8 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-014 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 617.15 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-015 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Apron | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 617.15 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-016 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1396.36 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-017 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1394.98 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-018 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-019 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1402.74 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-020 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone E1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 236.68 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-021 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1445.4 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-022 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1463.59 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-023 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-024 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1383.7 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-025 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-026 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1668.32 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-027 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1480.83 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-028 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1612.18 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-029 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-030 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1153.09 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-031 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1394.98 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-032 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-033 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1385.13 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-034 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-035 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1445.4 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-036 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1463.59 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-037 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1668.32 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-038 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1480.83 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-039 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-040 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1063.65 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-041 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-042 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1063.65 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-043 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | Party A | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-044 | Aircon Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | Party A | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-045 | Domestic Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | Party A | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-046 | Drinking Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | Party A | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 2 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-047 | Domestic Water Supply System for T1 | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | Party A | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | As-built drawing to be updated to include the additional booster system for Terminal 1 | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-048 | Foul Water Treatment Plant | STP System | Effleunt quality more than the allowable threshold. Poorly maintained system. Broken flowmeter. | Damage | Party BA | Third Party | General | General | All Zone | Foul Water Treatment Plant | Environment | 1990 | 4 | 3 | 3 | 4 | 3 | Upgrade the STP to BNR treatment process and should complied with latest DAO regulation. | 4 | 1 | lot | 1 | 24543300 |  | 1 | 0 | 0 | 0 | 24543300 | 0 | 0
RAS-049 | MVAC Ducting and Appurtenances | MVAC System | Ducting and appurtenances have good insulation and no leaks were detected |  | Party A | Third Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-125 | Chiller System | MVAC System | Chiller system in good condition, no visible leaks detected |  | Party A | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-126 | Cooling Tower System | MVAC System | Noticeable corrosion on the body of the cooling towers | Damage | Party A | Third Party | Terminal 2 | Others | Other | Utility Building | Mechanical | 2018 | 3 | 3 | 2 | 2 | 1 | Repainting | 2 | 4 | unit | 1 | 25000 |  | 1 | 0 | 0 | 0 | 100000 | 0 | 0
RAS-127 | Chiller 'Pump System | MVAC System | Pump System still in good condition except for a 1 rotary pump |  | Party A | Third Party | Terminal 2 | Others | Other | Utility Building | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 10 | unit | 0.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-128 | Computer Room Air-Conditioning System | MVAC System | Asset in good condition |  | Party A | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 9 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-129 | Primary Air Handling Unit | MVAC System | Asset in good condition |  | Party A | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-130 | Air Handling Unit | MVAC System | Asset in good condition, drain lines needs to be properly colored or protection to avoid trip hazard. |  | Party A | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 2 | 40 | unit | 0.05 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-131 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | Party A | Third Party | Terminal 1 | Arrival | All Zone | General | Mechanical | 1990 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-001 | PBB 1 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin and Rotunda is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-002 | PBB 2 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-003 | PBB 3 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-004 | PBB 4 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-005 | PBB 5 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin and Rotunda is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-006 | PBB 6 | Passenger Boarding Bridge (PBB) | Condemned. Parts were cannibalized for other bridges. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 5 | 3 | 5 | 5 | 5 | Procure parts and restore bridge to ensure equipment is ready for use. | 5 | 1 | set | 0.3 | 50000000 |  | 1 | 0 | 0 | 0 | 15000000 | 0 | 0
JMR-007 | Weighing Conveyors - (53 units) | Baggage Handling System (BHS) | Weighing Conveyors are calibrated on an Annual basis. Calibration should increase to semi-annual period to assure load cell is properly calibrated. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 53 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
DDD-001 | Software for the BHS system | Baggage Handling System (BHS) | Software is outdated and may affect correct operation of equipment and the whole system. | Aging | Party A | Third Party | Terminal 1 | Others | All Zone | General | IT | 2015 | 4 | 4 | 4 | 4 | 3 | Renewal of software system for the BHS | 5 | 1 | lot | 1 | 500000 |  | 1 | 0 | 0 | 0 | 500000 | 0 | 0
JMR-008 | Delivery Conveyors - (8 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | assuming specialized softwares
JMR-009 | Power Curves - (22 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 22 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-010 | Plough Diverters (Horizontal) - (6 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-011 | Race Track (Make-up Carousel) - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-012 | Manual Encode Conveyors - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-013 | ETD Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-014 | CB (Clear Bag) Line - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-015 | Merge Conveyors - (1 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-016 | Reject Bag Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-017 | Automatic Tag Reader - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 6 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-018 | Race Track (Arrival Carousel) - (6 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 1 | Arrival, Apron | All Zone | Baggage Re-Claim | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-019 | Initial Check - Stand Alone Dual View X-Ray (Smith) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-020 | Initial Check - Stand Alone Dual View X-Ray (Smith) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-021 | Final Check - Automatic Tray Return System (Rapiscan) - (4 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Gangway | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-022 | In-Line Hold Baggage Screening (Rapiscan) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Final Check | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-023 | In-Line Hold Baggage Screening Confirmatory (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-024 | Delivery - Stand Alone Dual View (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-025 | Stand-Alone Hold Baggage Screening (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-026 | Employee Entrace - Dual View (Smith) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 1 | Departure | All Zone | Entrance | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-027 | Escalator ES-2 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Terminal Building | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-028 | Escalator ES-3 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Terminal Building | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-029 | Escalator ES-4 Hitachi | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-030 | Escalator ES-5 Hitachi | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-031 | Escalator ES-6 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-032 | Escalator ES-7 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-033 | Elevator PE-1 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-034 | Elevator PE-2 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-035 | Elevator PE-3 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-036 | Elevator PE-4 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-037 | Elevator PE-5 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-038 | Elevator PE-6 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-039 | Elevator PE-7 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-040 | Elevator PE-8 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-041 | SCADA - HVAC | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room) |  | Party A | Third Party | Terminal 1 | Apron | All Zone | SCADA Room | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-042 | SCADA - Electrical | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room) |  | Party A | Third Party | Terminal 1 | Apron | All Zone | SCADA Room | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-043 | SCADA - Baggage Handling System | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room). Note that BHS is a critical component of the airport and its IT Systems must be very secured. | Aging | Party A | Third Party | Terminal 1 | Apron, Buildup | All Zone | SCADA Room | IT | 2019 | 3 | 3 | 2 | 2 | 2 | Correct issue with Beumer software that equipment is available for use. This is for the integration of the entire airport system. This is considered as new investment including the software, hardwares (e.g. electrical wiring, IT supports). | 1 | 1 | lot | 1 | 20000000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 20000000
JMR-044 | FIDS | IT System (ITS) | FIDS Monitors installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2019 | 3 | 2 | 3 | 2 | 2 | Install outdoor FIDS in a reinforced setup that will withstand typhoons, OR practice un-installation of FIDS monitors one (1) day before arrival of typhoon. | 3 | 10 | unit | 1 | 280000 |  | 1 | 0 | 0 | 0 | 2800000 | 0 | 0
JMR-045 | CUTE | IT System (ITS) | UPS failed graceful shut-down of Computer Servers during power outtage and run of Generator Sets. This further damaged costly hardware, softwares, and the data/information that should be securely stored. |  | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Check-In Area | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-046 | CCTV | IT System (ITS) | CCTV equipment installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2019 | 3 | 3 | 3 | 2 | 2 | Install outdoor CCTVs in a reinforced setup that will withstand typhoons, OR practice un-installation of CCTV equipment one (1) day before arrival of typhoon. | 6 | 15 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 300000 | 0 | 0
JMR-047 | PBB C-13r | Passenger Boarding Bridge (PBB) | Slat Curtain on Cab Area Damaged. Damaged Anti-Collision Sensors and Anti-Shear Sensor was temporarily repaired. Recommend immediate replacement due ensure safety of bridge and aircraft during operation. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-048 | PBB C-13l | Passenger Boarding Bridge (PBB) | Damaged Anti-Collision Sensor was temporarily repaired. Recommend immediate replacement due to critical component on safety of bridge. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-049 | PBB C-12r | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cab Area | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-050 | PBB C-12l | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cab Area | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-051 | PBB C-21 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-052 | PBB C-22 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-053 | PBB C-23 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-054 | Weighing Conveyors - (48 units) | Baggage Handling System (BHS) | Weighing Conveyors are calibrated on an Annual basis. Calibration should increase to semi-annual period to assure load cell is properly calibrated. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 48 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-055 | Delivery Conveyors - (4 units) | Baggage Handling System (BHS) | One (1) line of conveyors are not operational due to repair works |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-056 | Power Curves - (31 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 31 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-057 | Plough Diverters (Horizontal) - (6 units) | Baggage Handling System (BHS) | Line-1 plough diverter not working due to issue with Beumer software problem |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 6 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-058 | Race Track (Make-up Carousel) - (2 units) | Baggage Handling System (BHS) | One (1) set of make-up carousel is not operational due to issue with MVXR (X-Ray) software |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-059 | Manual Encode Conveyors - (1 units) | Baggage Handling System (BHS) | Manual Encoding Station is manual mode due to issue with Beumer software problem |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-060 | ETD Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-061 | CB (Clear Bag) Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-062 | Merge Conveyors - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-063 | Vertical Sorter - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-064 | Reject Bag Line - (1 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-065 | Automatic Tag Reader - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-066 | Race Track (Arrival Carousel) - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | Party A | Third Party | Terminal 2 | Arrival, Apron | All Zone | Baggage Re-Claim | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-067 | Stand Alone Dual View X-Ray (Rapiscan) - (5 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure | All Zone | Check-In Hall | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 5 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-068 | In-Line Hold Baggage Screening (Rapiscan) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure | All Zone | Check-In Hall | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-069 | In-bound Check - Stand Alone Dual View X-Ray (Smith) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Gangway | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-070 | Over Size Baggage - Stand Alone Hold Baggage Screeening (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Final Check | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-071 | Employee Entrace - Dual View (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-072 | In-Line Hold Baggage Screening Confirmatory (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-073 | Explosive Trace Detector (ETD) - (Rapiscan) - (6 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 6 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-074 | Walk Through Metal Detectors (WTMD) - (*8 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | Party A | Third Party | Terminal 2 | Departure | All Zone | Entrance | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 8 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-075 | Escalator ES-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-076 | Escalator ES-4 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-077 | Escalator ES-6 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-078 | Escalator ES-7 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-079 | Escalator ES-8 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-080 | Escalator ES-9 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-081 | Escalator ES-10 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-082 | Escalator ES-11 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-083 | Escalator ES-12 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-084 | Escalator ES-13 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-085 | Escalator ES-14 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-086 | Elevator PE-1 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-087 | Elevator PE-2 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-088 | Elevator PE-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-089 | Elevator PE-4 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-090 | Elevator PE-5 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-091 | Elevator PE-6 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-092 | Elevator PE-7 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-093 | Elevator PE-8 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-094 | Elevator PE-9 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-095 | Elevator PE-10 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-096 | Elevator PE-11 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-097 | Elevator PE-12 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-098 | Elevator SE-1 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-099 | Elevator SE-2 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-100 | Elevator SE-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-101 | SCADA - HVAC | IT System (ITS) | Stand-alone setup. Not linked to Central System. May pose |  | Party A | Third Party | Terminal 2 | Apron | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-102 | SCADA - Electrical | IT System (ITS) | Stand-alone setup. Not linked to Central System |  | Party A | Third Party | Terminal 2 | Apron | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-103 | SCADA - Baggage Handling System | IT System (ITS) | Stand-alone setup. Not linked to Central System. Problem with Beumer Program. |  | Party A | Third Party | Terminal 2 | Apron, Buildup | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-104 | FIDS | IT System (ITS) | FIDS Monitors installed outdoors are lost/damaged due to typhoon. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-105 | CUTE | IT System (ITS) | UPS failed graceful shut-down of Computer Servers during power outtage and run of Generator Sets. This further damaged costly hardware, softwares, and the data/information that should be securely stored. |  | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Check-In Area | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-106 | CCTV | IT System (ITS) | CCTV equipment installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | Party A | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2018 | 3 | 3 | 3 | 2 | 2 | Install outdoor CCTVs in a reinforced setup that will withstand typhoons, OR practice un-installation of CCTV equipment one (1) day before arrival of typhoon. | 3 | 15 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 300000 | 0 | 0
JMR-107 | AOCC | IT System (ITS) | SCADA of BHS, VAC, Utilities are not integrated. |  | Party A | Third Party | Terminal 2 | Departure | All Zone | Central Control Room | IT | 2018 | 3 | 3 | 1 | 1 | 2 | Cost already included in JMR-044 | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JCF-001 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 445.65 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 802170 | 0 | 0 | This is also recommended by the seller
JCF-002 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 883.93 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1591074 | 0 | 0
JCF-003 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 305.84 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 550512 | 0 | 0
JCF-004 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1064.43 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1915974 | 0 | 0
JCF-005 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 913.85 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1644930 | 0 | 0
JCF-006 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1383.54 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2490372 | 0 | 0
JCF-007 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1154.06 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2077308 | 0 | 0
JCF-008 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1113.7 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2004660 | 0 | 0
JCF-009 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 992.1 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1785780 | 0 | 0
JCF-010 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1382.79 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2489022 | 0 | 0
JCF-011 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1155.58 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2080044 | 0 | 0
JCF-012 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1215.21 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2187378 | 0 | 0
JCF-013 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1016.77 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1830186 | 0 | 0
JCF-014 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1383.41 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2490138 | 0 | 0
JCF-015 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 484.55 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 872190 | 0 | 0
JCF-016 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1431.54 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2576772 | 0 | 0
JCF-017 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1697.69 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3055842 | 0 | 0
JCF-018 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1700.03 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3060054 | 0 | 0
JCF-019 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1428.08 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2570544 | 0 | 0
JCF-020 | Waterproofing | Roofing System | Waterproofing reached its end of life resulting to water leak on the below level | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone E4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Reapplication of waterproofing | 4 | 1575.71 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 0 | 472713 | 0 | 0
JCF-021 | Waterproofing | Roofing System | Waterproofing reached its end of life resulting to water leak on the below level | Aging | Party A | Internal Team | Terminal 1 | Departure | Zone F3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Reapplication of waterproofing | 4 | 1575.04 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 0 | 472512 | 0 | 0
JCF-022 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 445.65 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 2228.25 | 0 | 0
JCF-023 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 883.93 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4419.65 | 0 | 0
JCF-024 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 305.84 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1529.2 | 0 | 0
JCF-025 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1064.43 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5322.15 | 0 | 0
JCF-026 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 913.85 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4569.25 | 0 | 0
JCF-027 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.54 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6917.7 | 0 | 0
JCF-028 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1154.06 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5770.3 | 0 | 0
JCF-029 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1113.7 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5568.5 | 0 | 0
JCF-030 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 992.1 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4960.5 | 0 | 0
JCF-031 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1382.79 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6913.95 | 0 | 0
JCF-032 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1155.58 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5777.9 | 0 | 0
JCF-033 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1215.21 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6076.05 | 0 | 0
JCF-034 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1016.77 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5083.85 | 0 | 0
JCF-035 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.41 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6917.05 | 0 | 0
JCF-036 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 484.55 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 2422.75 | 0 | 0
JCF-037 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1431.54 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 7157.7 | 0 | 0
JCF-038 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1697.69 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8488.45 | 0 | 0
JCF-039 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1700.03 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8500.15 | 0 | 0
JCF-040 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1428.08 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 7140.4 | 0 | 0
JCF-041 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 445.65 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 178260 | 0 | 0
JCF-042 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 883.93 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 353572 | 0 | 0
JCF-043 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 305.84 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 122336 | 0 | 0
JCF-044 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1064.43 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 425772 | 0 | 0
JCF-045 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 913.85 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 365540 | 0 | 0
JCF-046 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1383.54 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553416 | 0 | 0
JCF-047 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1154.06 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 461624 | 0 | 0
JCF-048 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1113.7 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 445480 | 0 | 0
JCF-049 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 992.1 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 396840 | 0 | 0
JCF-050 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1382.79 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553116 | 0 | 0
JCF-051 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1155.58 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 462232 | 0 | 0
JCF-052 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1215.21 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 486084 | 0 | 0
JCF-053 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1016.77 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 406708 | 0 | 0
JCF-054 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1383.41 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553364 | 0 | 0
JCF-055 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 484.55 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 193820 | 0 | 0
JCF-056 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1431.54 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 572616 | 0 | 0
JCF-057 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1697.69 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 679076 | 0 | 0
JCF-058 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1700.03 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 680012 | 0 | 0
JCF-059 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1428.08 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 571232 | 0 | 0
JCF-060 | Chiller Structural Steel Supports | Equipment and Machinery Supports | 1) Chiller support are corroded 2) Paints faded away, resulting to steel supports exposed to weather | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A4 | Cooling Tower | Structural | 1990 | 4 | 4 | 3 | 3 | 1 | Conduct structural evaluation to assess the capacity of the support May undergo retrofitting to increase the strength Esnure proper maintenance for the paint coating | 5 | 305.84 | m2 | 1 | 500 |  | 1 | 0 | 1 | 0 | 0 | 152920 | 0
JCF-061 | Floor Drains | Floor System | Clogged Floor Drains | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone A4 | Passageway | Architectural | 1990 | 3 | 3 | 3 | 3 | 1 | Declogged floor drains, and ensure regular maintenace to avoid the accumulation of debris on the drains | 3 | 305.84 | m2 | 0.3 | 80 |  | 1 | 0 | 0 | 0 | 7340.16 | 0 | 0
JCF-062 | Floor Drains | Floor System | Clogged Floor Drains | Damage | Party A | Internal Team | Terminal 1 | Departure | Zone E1 | Passageway | Architectural | 1990 | 3 | 3 | 3 | 3 | 1 | Declogged floor drains, and ensure regular maintenace to avoid the accumulation of debris on the drains | 3 | 1431.54 | m2 | 0.05 | 80 |  | 1 | 0 | 0 | 0 | 5726.16 | 0 | 0
JCF-063 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 620.26 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1116468 | 0 | 0 | Arrival
JCF-064 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 954.61 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1718298 | 0 | 0
JCF-065 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 274.87 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 494766 | 0 | 0
JCF-066 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1146.19 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2063142 | 0 | 0
JCF-067 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 978.22 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1760796 | 0 | 0
JCF-068 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1389.9 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2501820 | 0 | 0
JCF-069 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1157.59 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2083662 | 0 | 0
JCF-070 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1128.74 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2031732 | 0 | 0
JCF-071 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1000.72 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1801296 | 0 | 0
JCF-072 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1390.72 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2503296 | 0 | 0
JCF-073 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1157.87 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2084166 | 0 | 0
JCF-074 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1250.95 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2251710 | 0 | 0
JCF-075 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1054.2 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1897560 | 0 | 0
JCF-076 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1389.08 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2500344 | 0 | 0
JCF-077 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 309.05 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 556290 | 0 | 0
JCF-078 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1356.4 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2441520 | 0 | 0
JCF-079 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1705.18 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3069324 | 0 | 0
JCF-080 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1705.04 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3069072 | 0 | 0
JCF-081 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | Party A | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1321.57 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2378826 | 0 | 0
JCF-082 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 620.26 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 3101.3 | 0 | 0
JCF-083 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 954.61 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4773.05 | 0 | 0
JCF-084 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 274.87 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1374.35 | 0 | 0
JCF-085 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1146.19 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5730.95 | 0 | 0
JCF-086 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 978.22 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4891.1 | 0 | 0
JCF-087 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1389.9 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6949.5 | 0 | 0
JCF-088 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1157.59 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5787.95 | 0 | 0
JCF-089 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1128.74 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5643.7 | 0 | 0
JCF-090 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1000.72 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5003.6 | 0 | 0
JCF-091 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1390.72 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6953.6 | 0 | 0
JCF-092 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1157.87 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5789.35 | 0 | 0
JCF-093 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1250.95 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6254.75 | 0 | 0
JCF-094 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1054.2 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5271 | 0 | 0
JCF-095 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1389.08 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6945.4 | 0 | 0
JCF-096 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 309.05 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1545.25 | 0 | 0
JCF-097 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1356.4 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6782 | 0 | 0
JCF-098 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1705.18 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8525.9 | 0 | 0
JCF-099 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1705.04 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8525.2 | 0 | 0
JCF-100 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1321.57 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6607.85 | 0 | 0
JCF-101 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 620.26 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 248104 | 0 | 0
JCF-102 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 954.61 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 381844 | 0 | 0
JCF-103 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 274.87 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 109948 | 0 | 0
JCF-104 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1146.19 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 458476 | 0 | 0
JCF-105 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 978.22 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 391288 | 0 | 0
JCF-106 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1389.9 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 555960 | 0 | 0
JCF-107 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1157.59 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 463036 | 0 | 0
JCF-108 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1128.74 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 451496 | 0 | 0
JCF-109 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1000.72 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 400288 | 0 | 0
JCF-110 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1390.72 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 556288 | 0 | 0
JCF-111 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1157.87 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 463148 | 0 | 0
JCF-112 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1250.95 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 500380 | 0 | 0
JCF-113 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1054.2 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 421680 | 0 | 0
JCF-114 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1389.08 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 555632 | 0 | 0
JCF-115 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 309.05 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 123620 | 0 | 0
JCF-116 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1356.4 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 542560 | 0 | 0
JCF-117 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1705.18 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 682072 | 0 | 0
JCF-118 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1705.04 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 682016 | 0 | 0
JCF-119 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | Party A | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1321.57 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 528628 | 0 | 0
JCF-120 | Facade Glazing | Curtain Wall System | Glazings and its supports was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 1 | Roof Level | Zone E4 | General | Architectural | 1990 | 5 | 5 | 3 | 3 | 2 | Replaced damaged facaded glazing | 6 | 1575.71 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 630284 | 0 | 0
JCF-121 | Facade Glazing | Curtain Wall System | Glazings and its supports was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 1 | Roof Level | Zone F3 | General | Architectural | 1990 | 5 | 5 | 3 | 3 | 2 | Replaced damaged facaded glazing | 6 | 1575.04 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 630016 | 0 | 0
JCF-122 | Roof Fabric Sheet, Roof Trusses, Main-Lateral-Frame-System | Structural Framing System | Structural code used for the design was oudated - may not comply to current standards for wind and seismic loadings | Aging | Party A | Internal Team | Terminal 1 | Roof Level | All Zone | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to increase the strength and meet the requirements for current structural code of the philippines | 7 | 1 | lot | 1 | 25000000 |  | 1 | 0 | 0 | 0 | 25000000 | 0 | 0
JCF-1221 | Retrofitting of the structure | Roof Structural Framing System | Damage with cracking and old design | Damage | Party BA | Internal Team | Terminal 1 | General | All Zone | General | Structural | 1994 | 3 | 3 | 3 | 3 | 3 | Structureal Reforitting | 4 | 1 | lot | 1 | 105000000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 105000000
JCF-181 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration deterioration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | Party A | Internal Team | Terminal 2 | Apron | All Zone | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Conduct storm drain study to assess the need to provide additional drainage system on the area. Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 7 | 1 | lot | 1 | 2000000 |  | 1 | 0 | 0 | 0 | 2000000 | 0 | 0
JCF-183 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 550.29 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 55029 | 0 | 0
JCF-184 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 58971 | 0 | 0
JCF-185 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1439.77 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 143977 | 0 | 0
JCF-186 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone B3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1509.96 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 150996 | 0 | 0
JCF-187 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 550.29 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 110058 | 0 | 0
JCF-188 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 117942 | 0 | 0
JCF-189 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1439.77 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 287954 | 0 | 0
JCF-190 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 647.47 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 129494 | 0 | 0
JCF-191 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 697.8 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 139560 | 0 | 0
JCF-192 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1502.34 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 300468 | 0 | 0
JCF-193 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1464.13 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 292826 | 0 | 0
JCF-194 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1591.09 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 318218 | 0 | 0
JCF-195 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1594.09 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 318818 | 0 | 0
JCF-196 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1128.22 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 225644 | 0 | 0
JCF-197 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1130.82 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 226164 | 0 | 0
JCF-198 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 756.73 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 151346 | 0 | 0
JCF-199 | Beam | Structural Framing System | Damaged and exposed rebar of beam due to removal of canopy | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 5 | 5 | 4 | 4 | 2 | Conduct structural investigation to assess the strength of the structural membder Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 117942 | 0 | 0
JCF-200 | Louver Support | Architectural Elements Supports | Louver support starting to shows corrosion | Aging | Party A | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 1 | 1 | 1 | Repplication of paint to protect the structural steel support from weather | 3 | 589.71 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5897.1 | 0 | 0
JCF-201 | Louver Support | Architectural Elements Supports | Louver support starting to shows corrosion | Aging | Party A | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 1 | 1 | 1 | Repplication of paint to protect the structural steel support from weather | 3 | 550.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5502.9 | 0 | 0
JCF-202 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Apron | Zone A3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 5 | 474.94 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 23747 | 0 | 0
JCF-203 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Apron | Zone C1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 5 | 518.69 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 25934.5 | 0 | 0
JCF-204 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Apron | Zone C3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 3 | 712.12 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 35606 | 0 | 0
JCF-205 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone D1 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 1420.77 | m2 | 0.02 | 1000 |  | 1 | 0 | 0 | 0 | 28415.4 | 0 | 0
JCF-206 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone D3 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 1417.29 | m2 | 0.02 | 1000 |  | 1 | 0 | 0 | 0 | 28345.8 | 0 | 0
JCF-207 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C1 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 518.69 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 51869 | 0 | 0
JCF-208 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C3 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 712.12 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 71212 | 0 | 0
JCF-209 | Mesh Ceiling | Ceiling System | Traces of water/liquid leak on the mesh ceiling | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A4 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Cleaning of the affected mesh ceiling and replacement of the piping that causes the leak | 3 | 1439.77 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2879.54 | 0 | 0
JCF-210 | Mesh Ceiling | Ceiling System | Dismantled mesh ceiling that was affected by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Apron | Zone B3 | General | Architectural | 2018 | 2 | 2 | 1 | 1 | 1 | Replaced dismantled roofing sheet | 4 | 1509.96 | m2 | 0.15 | 500 |  | 1 | 0 | 0 | 0 | 113247 | 0 | 0
JCF-211 | Beam | Structural Framing System | Deflection on beam that possibly cause of poor construction | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1439.77 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 143977 | 0 | 0
JCF-212 | Floor Tiles | Floor System | There were holes on the floor tiles due to the removal of the luggage cart balustrade | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C2 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Fill in holes or replacement of the affected tile panel | 3 | 1384.87 | m2 | 0.02 | 400 |  | 1 | 0 | 0 | 0 | 11078.96 | 0 | 0
JCF-213 | Floor Tiles | Floor System | There were holes on the floor tiles due to the removal of the luggage cart balustrade | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C4 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Fill in holes or replacement of the affected tile panel | 3 | 1383.23 | m2 | 0.02 | 400 |  | 1 | 0 | 0 | 0 | 11065.84 | 0 | 0
JCF-214 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1439.77 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14397.7 | 0 | 0
JCF-215 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1509.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15099.6 | 0 | 0
JCF-216 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1384.87 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13848.7 | 0 | 0
JCF-217 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.23 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13832.3 | 0 | 0
JCF-218 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1420.77 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14207.7 | 0 | 0
JCF-219 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1417.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14172.9 | 0 | 0
JCF-220 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 260.66 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2606.6 | 0 | 0
JCF-221 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 647.47 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6474.7 | 0 | 0
JCF-222 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 263.84 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2638.4 | 0 | 0
JCF-223 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 697.8 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6978 | 0 | 0
JCF-224 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1502.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15023.4 | 0 | 0
JCF-225 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1464.13 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14641.3 | 0 | 0
JCF-226 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1591.09 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15910.9 | 0 | 0
JCF-227 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1594.09 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15940.9 | 0 | 0
JCF-228 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1128.22 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11282.2 | 0 | 0
JCF-229 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1130.82 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11308.2 | 0 | 0
JCF-230 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 756.73 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7567.3 | 0 | 0
JCF-231 | Elevator | Vertical Transport System | 1) Damage on the metal casing According to the Party A this elevator was damage because of the rescue operation made during the time that somebody got trap and the elevator doors are not opening | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone E4 | General | Mechanical | 2018 | 3 | 3 | 2 | 2 | 2 | Repair aluminum sheet casing of the elevator Check and investigate the operating system of the elevator that causes the machine to stop opening | 3 | 697.8 | m2 | 1 | 200 |  | 1 | 0 | 0 | 0 | 139560 | 0 | 0
JCF-232 | Facade Glazing | Curtain Wall System | Glazing panel cracked due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 6 | 538.88 | m2 | 0.05 | 5000 |  | 1 | 0 | 0 | 0 | 134720 | 0 | 0
JCF-233 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1396.36 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 209454 | 0 | 0
JCF-234 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1394.98 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83698.8 | 0 | 0
JCF-235 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1402.74 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 210411 | 0 | 0
JCF-236 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1385.13 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83107.8 | 0 | 0
JCF-237 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 538.88 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 80832 | 0 | 0
JCF-238 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 618.73 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 92809.5 | 0 | 0
JCF-239 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1445.4 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 216810 | 0 | 0
JCF-240 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1463.59 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 219538.5 | 0 | 0
JCF-241 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 266.61 | m2 | 1 | 300 |  | 1 | 0 | 0 | 0 | 79983 | 0 | 0
JCF-242 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1383.7 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 207555 | 0 | 0
JCF-243 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1668.32 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 250248 | 0 | 0
JCF-244 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1480.83 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 222124.5 | 0 | 0
JCF-245 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1612.18 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 241827 | 0 | 0
JCF-246 | Suspended Slab | Structural Slab System | Severe crack near Grid Line 11L | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Structural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1612.18 | m2 | 0.1 | 300 |  | 1 | 0 | 0 | 0 | 48365.4 | 0 | 0
JCF-247 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1063.65 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 159547.5 | 0 | 0
JCF-248 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1089.45 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 163417.5 | 0 | 0
JCF-249 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 727.96 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 109194 | 0 | 0
JCF-250 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone K1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1153.09 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 172963.5 | 0 | 0
JCF-251 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone K3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 995.26 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 149289 | 0 | 0
JCF-252 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 416.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 83356 | 0 | 0
JCF-253 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 473.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 94756 | 0 | 0
JCF-254 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1092.48 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 218496 | 0 | 0
JCF-255 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 538.88 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 107776 | 0 | 0
JCF-256 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 618.73 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 123746 | 0 | 0
JCF-257 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1445.4 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 289080 | 0 | 0
JCF-258 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1463.59 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 292718 | 0 | 0
JCF-259 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1668.32 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 333664 | 0 | 0
JCF-260 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1480.83 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 296166 | 0 | 0
JCF-261 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1063.65 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 212730 | 0 | 0
JCF-262 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1089.45 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 217890 | 0 | 0
JCF-263 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 727.96 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 145592 | 0 | 0
JCF-264 | Beam | Structural Framing System | Damaged and exposed rebar of beam due to removal of canopy | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone B1 | General | Structural | 2018 | 5 | 5 | 4 | 4 | 3 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 5 | 473.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 94756 | 0 | 0
JCF-265 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1092.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10924.8 | 0 | 0
JCF-266 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1117.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11178.3 | 0 | 0
JCF-267 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1396.36 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13963.6 | 0 | 0
JCF-268 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1394.98 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2789.96 | 0 | 0
JCF-269 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1402.74 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14027.4 | 0 | 0
JCF-270 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1385.13 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2770.26 | 0 | 0
JCF-271 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 236.68 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2366.8 | 0 | 0
JCF-272 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 538.88 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5388.8 | 0 | 0
JCF-273 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 263 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2630 | 0 | 0
JCF-274 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 618.73 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6187.3 | 0 | 0
JCF-275 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1445.4 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14454 | 0 | 0
JCF-276 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1463.59 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14635.9 | 0 | 0
JCF-277 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1668.32 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 16683.2 | 0 | 0
JCF-278 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1480.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14808.3 | 0 | 0
JCF-279 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1063.65 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10636.5 | 0 | 0
JCF-280 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1089.45 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10894.5 | 0 | 0
JCF-281 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 727.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7279.6 | 0 | 0
JCF-282 | Internal Walls | Wall System | Exposed plastic mesh reinforcement of wall due to poor construction | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G2 | Baggage Handling Area | Architectural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the damaged areas and repainting of walls to cover epoxy patched areas | 3 | 1480.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14808.3 | 0 | 0
JCF-283 | Facade Glazing | Curtain Wall System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone A4 | Vestibule | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 5 | 1116.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11163.4 | 0 | 0
JCF-284 | Facade Glazing | Curtain Wall System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone B3 | Vestibule | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 5 | 1194.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11944.8 | 0 | 0
JCF-285 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone C2 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1374.41 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34360.25 | 0 | 0
JCF-286 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone C4 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1409.6 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 35240 | 0 | 0
JCF-287 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone D1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1391.84 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34796 | 0 | 0
JCF-288 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone D3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1393.01 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34825.25 | 0 | 0
JCF-289 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1431.02 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 35775.5 | 0 | 0
JCF-290 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1641.36 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 41034 | 0 | 0
JCF-291 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1556.69 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 38917.25 | 0 | 0
JCF-292 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone G3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1677.45 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 41936.25 | 0 | 0
JCF-293 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone K1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1091.98 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 27299.5 | 0 | 0
JCF-294 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Departure | Zone K3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1084 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 27100 | 0 | 0
JCF-295 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | Party A | Internal Team | Terminal 2 | Departure | Zone A2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 409.62 | m2 | 1 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 409620
JCF-296 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | Party A | Internal Team | Terminal 2 | Departure | Zone B1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 455.62 | m2 | 1 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 455620
JCF-297 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | Party A | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 1116.34 | m2 | 0.5 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 558170
JCF-298 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | Party A | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 1194.48 | m2 | 0.5 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 597240
JCF-299 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1431.02 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 71551 | 0 | 0
JCF-300 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1556.69 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 77834.5 | 0 | 0
JCF-301 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1641.36 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 82068 | 0 | 0
JCF-302 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1677.45 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 83872.5 | 0 | 0
JCF-303 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1463.59 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 73179.5 | 0 | 0
JCF-304 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1668.32 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 83416 | 0 | 0
JCF-305 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1383.7 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 69185 | 0 | 0
JCF-306 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1612.18 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 80609 | 0 | 0
JCF-307 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1092.48 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 327744
JCF-308 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1117.83 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 335349
JCF-309 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1396.36 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 977452
JCF-310 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1402.74 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 981918
JCF-311 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1394.98 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 976486
JCF-312 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1385.13 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 969591
JCF-313 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 538.88 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 161664
JCF-314 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 618.73 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 185619
JCF-315 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1445.4 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1011780
JCF-316 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1463.59 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1024513
JCF-317 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1383.7 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 968590
JCF-318 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1668.32 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1167824
JCF-319 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1480.83 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1036581
JCF-320 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1612.18 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1128526
JCF-321 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1063.65 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 744555
JCF-322 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1089.45 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 762615
JCF-323 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 727.96 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 509572
JCF-324 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone K1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1153.09 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 807163
JCF-325 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Arrival | Zone K3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 995.26 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 696682
JCF-326 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1116.34 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 334902
JCF-327 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1194.48 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 358344
JCF-328 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1374.41 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 962087
JCF-329 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1391.84 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 974288
JCF-330 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1409.6 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 986720
JCF-331 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1393.01 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 975107
JCF-332 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 608.56 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 182568
JCF-333 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 667.72 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 200316
JCF-334 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1510.96 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1057672
JCF-335 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1431.02 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1001714
JCF-336 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1641.36 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1148952
JCF-337 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1556.69 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1089683
JCF-338 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1347.9 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 943530
JCF-339 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1677.45 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1174215
JCF-340 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1372.29 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 960603
JCF-341 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1104.62 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 773234
JCF-342 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone I1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 758.15 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 530705
JCF-343 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone K1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1091.98 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 764386
JCF-344 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone K3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1084 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 758800
JCF-345 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1374.41 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 206161.5 | 0 | 0
JCF-346 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1409.6 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 84576 | 0 | 0
JCF-347 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1391.84 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 208776 | 0 | 0
JCF-348 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1393.01 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83580.6 | 0 | 0
JCF-349 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 608.56 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 91284 | 0 | 0
JCF-350 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 667.72 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 100158 | 0 | 0
JCF-351 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1510.96 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 226644 | 0 | 0
JCF-352 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1431.02 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 214653 | 0 | 0
JCF-353 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1641.36 | m2 | 1 | 300 |  | 1 | 0 | 0 | 0 | 492408 | 0 | 0
JCF-354 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1641.36 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 246204 | 0 | 0
JCF-355 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1556.69 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 233503.5 | 0 | 0
JCF-356 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1347.9 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 202185 | 0 | 0
JCF-357 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1677.45 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 251617.5 | 0 | 0
JCF-358 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1372.29 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 205843.5 | 0 | 0
JCF-359 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1104.62 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 165693 | 0 | 0
JCF-360 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 758.15 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 113722.5 | 0 | 0
JCF-361 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone K1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1091.98 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 163797 | 0 | 0
JCF-362 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone K3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1084 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 162600 | 0 | 0
JCF-363 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 608.56 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 547704 | 0 | 0
JCF-364 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 667.72 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 600948 | 0 | 0
JCF-365 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1510.96 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1359864 | 0 | 0
JCF-366 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1431.02 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1287918 | 0 | 0
JCF-367 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1641.36 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1477224 | 0 | 0
JCF-368 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1556.69 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1401021 | 0 | 0
JCF-369 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1347.9 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1213110 | 0 | 0
JCF-370 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1677.45 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1509705 | 0 | 0
JCF-371 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1372.29 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1235061 | 0 | 0
JCF-372 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1104.62 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 994158 | 0 | 0
JCF-373 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 758.15 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 682335 | 0 | 0
JCF-374 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1116.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11163.4 | 0 | 0
JCF-375 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1194.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11944.8 | 0 | 0
JCF-376 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1374.41 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13744.1 | 0 | 0
JCF-377 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1409.6 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14096 | 0 | 0
JCF-378 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1391.84 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13918.4 | 0 | 0
JCF-379 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1393.01 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13930.1 | 0 | 0
JCF-380 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 232.62 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2326.2 | 0 | 0
JCF-381 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 608.56 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6085.6 | 0 | 0
JCF-382 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 261.19 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2611.9 | 0 | 0
JCF-383 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 667.72 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6677.2 | 0 | 0
JCF-384 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1510.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15109.6 | 0 | 0
JCF-385 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1431.02 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14310.2 | 0 | 0
JCF-386 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1556.69 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15566.9 | 0 | 0
JCF-387 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1347.9 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13479 | 0 | 0
JCF-388 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1372.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13722.9 | 0 | 0
JCF-389 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1104.62 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11046.2 | 0 | 0
JCF-390 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | Party A | Internal Team | Terminal 2 | Departure | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 758.15 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7581.5 | 0 | 0
JCF-391 | Pipe | Equipment and Machinery Supports | no lateral support between two (2) floors | Others | Party A | Internal Team | Terminal 2 | Arrival | Zone G1 | Lobby | Structural | 2018 | 2 | 2 | 2 | 2 | 1 | Provide lateral supports | 3 | 1668.32 | m2 | 0.01 | 80 |  | 1 | 0 | 0 | 0 | 1334.656 | 0 | 0
JCF-392 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1502.34 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 60093.6 | 0 | 0
JCF-393 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone F2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1464.13 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 58565.2 | 0 | 0
JCF-394 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1591.09 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 63643.6 | 0 | 0
JCF-395 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone G2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1594.09 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 63763.6 | 0 | 0
JCF-396 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1128.22 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 45128.8 | 0 | 0
JCF-397 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone H2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1130.82 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 45232.8 | 0 | 0
JCF-398 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Terminal 2 | Apron | Zone I1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 756.73 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 30269.2 | 0 | 0
JCF-399 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP111 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 10800 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 432000 | 0 | 0
JCF-400 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP112 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 10800 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 432000 | 0 | 0
JCF-401 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP113 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-402 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP114 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-403 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP115 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-404 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP116 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-405 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | Party A | Internal Team | Airside | Outside Terminal | AP117 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-406 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP118 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-407 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP119 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-408 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP120 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-409 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP121 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-410 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP122 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-411 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP123 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 13500 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 540000 | 0 | 0
JCF-412 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP124 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 13500 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 540000 | 0 | 0
JCF-413 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | Party A | Internal Team | Airside | Outside Terminal | AP211 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-414 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | Party A | Internal Team | Airside | Outside Terminal | AP212 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-415 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP213 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-416 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP214 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-417 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | Party A | Internal Team | Airside | Outside Terminal | AP215 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-418 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | Party A | Internal Team | Airside | Outside Terminal | AP216 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-419 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP217 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-420 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP218 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-421 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP219 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-422 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP220 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-423 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP221 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-424 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | Party A | Internal Team | Airside | Outside Terminal | AP222 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-425 | Louver | Louvers and Vent | Missing louver pannel due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Landside | Outside Terminal | R1003 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Replacement of detached louvers | 5 | 3555 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 533250 | 0 | 0
JCF-426 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | R1011 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 1110 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 666000 | 0 | 0
JCF-427 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | R1012 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 840 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 504000 | 0 | 0
JCF-428 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | R1013 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 350 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 210000 | 0 | 0
JCF-429 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | R1014 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 880 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 528000 | 0 | 0
JCF-430 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P101 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-431 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P105 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-432 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P109 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-433 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P113 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-434 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P117 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-435 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P120 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-436 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P121 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-437 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P122 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-438 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | Party A | Internal Team | Landside | Outside Terminal | P123 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-439 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Landside | Outside Terminal | T122 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.6 | 1000 |  | 1 | 0 | 0 | 0 | 237000 | 0 | 0
JCF-440 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Landside | Outside Terminal | T123 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.6 | 1000 |  | 1 | 0 | 0 | 0 | 237000 | 0 | 0
JCF-441 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Landside | Outside Terminal | T126 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.2 | 1000 |  | 1 | 0 | 0 | 0 | 79000 | 0 | 0
JCF-442 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Roof Level | Zone I1 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 758.15 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 75815 | 0 | 0
JCF-443 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Roof Level | Zone G2 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 1347.9 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 134790 | 0 | 0
JCF-444 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | Party A | Internal Team | Terminal 2 | Roof Level | Zone K1 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 1091.98 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 109198 | 0 | 0
Note on X106: +5000 if structural members is included
Note on A241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Federizo, Joseph